**Appendices**

**Instructions & Inspection and Maintenance Plan Template Appendix**

**Appendix A**

Stormwater Maintenance Agreement Template

**Appendix B**

General Location and Description of Stormwater Management Facilities Example

**Appendix C**

Standard Operation Procedures for:

Extended Detention Basins (EDBs)

Grass Buffers and Grass Swales (GB-GS)

Bioretention (BRCs) aka Porous Landscape Detention (PLDs)

Sand Filter Basins (SFBs)

**Appendix D**

Inspection Forms

**Appendix E**

Maintenance Forms

**Appendix F**

Annual Inspection and Maintenance Reporting Form

**Appendix G**

Inspection and Maintenance Site Plan(s) Check Lists

**Instructions and Maintenance Plan Template Appendix**

**Instructions for Preparing a Stormwater Facility Inspection & Maintenance Plan (I & M Plan)**

**Stormwater Management Facility Inspection and Maintenance (I&M) Plan Template**

**Instructions for Preparing a Stormwater Facility**

**Inspection & Maintenance Plan (I & M Plan)**

Inspection and Maintenance (I & M) Plans are required to be provided for all permanent water quality Best Management Practices (BMPs) installed on a site. See City Code Section 138-442.5(c). The purpose of the I & M Plan is to provide information to the person or entity responsible for inspection and maintenance of the facility to ensure the facility is adequately maintained to function as designed. The information provided in the I & M will help the maintenance personnel understand the facility; will provide guidance for inspection and maintenance operations specific to the type of facility; and will provide mechanisms for ensuring the long-term maintenance of the facility is performed.

Preparing the I & M Plan

1. Access the I and M Plan Template at: [www.auroragov.org](http://www.auroragov.org), business services, development center, Water & Other Utilities – Forms from Rules and Regulations – open the zip file and choose the I and M Plan Template.
2. Download the I & M Plan template, and insert the project specific information on the Title Sheet.
3. Download the Stormwater Maintenance Agreement template. Insert the project specific information, execute, and submit the document to the City of Aurora Water staff for recordation. Do this for as many agreements needed. Obtain copies of the fully executed and recorded Stormwater Maintenance Agreement(s) for the project and include in Appendix A
4. Download Appendix B and insert the project specific information.
5. Download the Standard Operating Procedure (SOP) for the specific type(s) of permanent BMPs contained on the project (this document is generic and requires no additional information unless the BMP differs significantly from the standard).
6. Download the Inspection and Maintenance forms for each permanent BMP facility type.
7. Download the Annual Inspection and Maintenance Reporting Form.
8. Prepare a Stormwater Facilities Map in conformance with the Stormwater Facilities example drawing and checklist.
9. Prepare Stormwater Facility Plans and Detail Drawings for each storm water facility, in accordance with the Example Drawings and Checklists for Stormwater Facility Plans and Details.

Assemble the I & M Plan in the following order:

Title Sheet

Stormwater Management Facility Inspection and Maintenance Plan

Appendix A – Maintenance Agreement(s)

Appendix B – Description of Stormwater Facilities

Appendix C – BMP Facility SOPs (for each type of facility)

Appendix D – Inspection Form for each facility

Appendix E – Maintenance Form for each type of facility

Appendix F – Annual Inspection and Maintenance Reporting Form

Appendix G – Stormwater Facilities map; Facility Plan and Detail Drawings

One copy of the completed I & M Plan shall be provided to the City of Aurora prior to approval of the Civil Construction Plans.

****

**Stormwater Management Facility**

**Inspection and Maintenance (I&M) Plan**

**Template**

**for:**

***Insert Development***

**Located at:**

***Insert Address***

**Prepared for:**


***Insert Property Owner Name, Address and Phone No.***

**Prepared by:**

***Insert Name; Address, Phone No. and email address***

***Insert Date Prepared***

|  |  |
| --- | --- |
| **APPROVED ON THIS DATE** | |
| **City Engineer** | **Date** |
| **Aurora Water Department** | **Date** |



**Reference:**

**This plan is adapted from Southeast Metro Stormwater Authority, *Operation and Maintenance (O & M) Manual,* and Town of Parker, Colorado, *Stormwater Permanent Best Management Practices (PBMP) Long-Term Operation and Maintenance Manual*, October 2004**

**Stormwater Management Facility**

**Inspection and Maintenance (I&M) Plan**

# **Table of Contents**

1. Compliance with Stormwater Facility Maintenance Requirements
2. Inspection & Maintenance- Annual Reporting
3. Preventative Measures to Reduce Maintenance Costs
4. Access and Easements
5. Safety
6. Field Inspection Equipment
7. Inspecting Stormwater Management Facilities

A. Inspection Procedures

B. Inspection Report

C. Verification of Inspection and Form Submittal

1. Maintaining Stormwater Management Facilities

A. Maintenance Categories

B. Maintenance Personnel

C. Maintenance Forms

# **Appendices**

## **Appendix A -** Maintenance Agreement(s)

**Appendix B -** Description of Stormwater Management Facilities

**Appendix C** - Standard Operation Procedures (SOP) for Extended Detention Basins; Grass Buffers and Grass Swales; Bioretention Cells aka Porous Landscape Detention; and Sand Filter Basin BMPs

**Appendix D -** Inspection Form(s)

**Appendix E -** Maintenance Form(s)

**Appendix F -** Annual Inspection and Maintenance Submittal form

**Appendix G** -Stormwater Facilities Map; Facility plan and detail sheets

**Stormwater Management Facility**

**Inspection and Maintenance (I&M) Plan**

1. Compliance with Stormwater Facility Maintenance Requirements

All property owners are responsible for ensuring stormwater facilities installed on their property are properly maintained and function as designed. <<Insert Property Owner’s Name>> may elect to assign many of the management and maintenance functions described in this plan to a third party. <<Insert Property Owner’s Name>> is aware of their responsibilities regarding stormwater facility maintenance. Maintenance agreement(s) associated with this property are provided in Appendix A.

1. **Inspection & Maintenance – Annual Reporting**

Requirements for the inspection and maintenance of stormwater facilities, as well as reporting requirements are included in this Stormwater Management Facility Inspection and Maintenance (I&M) Plan.

**Verification that the stormwater facilities have been properly inspected and maintained; submittal of the required Inspection and Maintenance Forms, and Inspector qualifications shall be provided to the City of Aurora on an annual basis. The annual reporting form shall be provided to the City of Aurora prior to May 31 of each year.**

Copies of the Inspection and Maintenance forms for each of the stormwater facilities are located in Appendix D and E. A standard annual reporting form is provided in Appendix F. Each form shall be reviewed and submitted by the property owner or property manager to:

City of Aurora

Aurora Water – Environmental Services

15151 E. Alameda Parkway, Ste. 2500

Aurora, CO 80012

[envservices@auroragov.org](mailto:envservices@auroragov.org)

1. Preventative Measures to Reduce Maintenance Costs

The most effective way to maintain your water quality facility is to prevent the pollutants from entering the facility in the first place. Common pollutants include sediment, trash and debris, chemicals, dog waste, runoff from stored materials, illicit discharges into the storm drainage system and many others. <<Insert Property Owner’s Name>> maintenance program includes measures to address these potential contaminants. Depending on the storm water quality facilities installed on the site the maintenance program includes:

* Educate property owners/residents to be aware of how their actions affect water quality, and how they can help reduce maintenance costs.
* Keep properties, streets and gutters, and parking lots free of trash, debris, and lawn clippings.
* Ensure the proper disposal of hazardous wastes and chemicals.
* Plan lawn care to minimize the use of chemicals and pesticides.
* Sweep paved surfaces regularly and dispose the sweepings properly.
* Be aware of automobiles leaking fluids. Use absorbents such as cat litter to soak up drippings – dispose of properly.
* Re-vegetate disturbed and bare areas to maintain vegetative stabilization.
* Clean out the upstream components of the storm drainage system, including inlets, storm sewers and outfalls.
* Do not store materials outdoors (including landscaping materials) unless properly protected from runoff.

1. Access and Easements

<<Insert Property Owner’s Name>> shall prepare a drawing showing all stormwater management facilities located on the site including designated access locations as well as a required easements. Refer to the Stormwater Facilities Map located in Appendix G for access and easement locations.

1. Safety

Keep safety considerations at the forefront of inspection procedures at all times. Likely hazards should be anticipated and avoided. <<Insert Property Owner’s Name>> personnel should never enter a confined space (outlet structure, manhole, etc.) without proper training or equipment. A confined space should never be entered without at least one additional person present and without using appropriate personal protection equipment.

If a toxic or flammable substance is discovered, leave the immediate area and call 911.

Vertical drops and fall hazards may be encountered in areas located within and around the facility. <<Insert Property Owner’s Name>> shall avoid walking on top of retaining walls or other structures that have a significant vertical drop. If a vertical drop is identified that is greater than forty-eight inches (48”) in height, make the appropriate note/comment on the maintenance inspection form.

**If any hazard is found within the facility area that poses an immediate threat to public safety, call 911.**

1. Field Inspection Equipment

<<Insert Property Owner’s Name>> inspectors shall have the appropriate equipment to take to the field. This is to ensure the safety of the inspector and allow the inspections to be performed as efficiently as possible. Below is a list of the equipment that may be necessary to perform the inspections of all Stormwater Management Facilities:

* Protective clothing and boots.
* Safety equipment (vest, hard hat, confined space entry equipment).
* Communication equipment.
* Inspection and Maintenance Plan for the site including stormwater management facility location maps.
* Clipboard.
* Stormwater Facility Maintenance Inspection Forms (See Appendix D).
* Manhole Lid Remover.
* Shovel.

Some of the items identified above need not be carried by the inspector (manhole lid remover, shovel, and confined space entry equipment). However, this equipment should be available in the vehicle driven to the site.

1. Inspecting Stormwater Management Facilities

The quality of stormwater entering the waters of the state relies heavily on the proper operation and maintenance of permanent best management practices. Stormwater management facilities shall be periodically inspected to ensure they function as designed. The inspection will determine the appropriate maintenance required for the facility.

A. Inspection Procedures

All stormwater management facilities shall be inspected by a qualified individual at a minimum of once per year. See the City of Aurora *Storm Drainage Design & Technical Criteria* Manual for general guidelines for an inspector. Inspections will follow the inspection guidance found in the SOP for the specific type of facility. (Appendix C of this plan).

B. Inspection Report

<<Insert Property Owner’s Name>> personnel or inspector conducting the inspection activities shall complete the appropriate inspection report for the specific facility. Inspection reports are located in Appendix D.

#### The following information explains how to fill out the Inspection Forms:

#### General Information

This section identifies the facility location, person conducting the inspection, the date and time the facility was inspected, and approximate days since the last rainfall. Property classification is identified as single-family residential, multi-family residential, commercial, or other.

The reason for the inspection is also identified on the form depending on the nature of the inspection. All facilities shall be inspected on an annual basis at a minimum. In addition, all facilities shall be inspected after a significant precipitation event to ensure the facility is draining appropriately and to identify any damage that occurred as a result of the increased runoff.

Inspection Scoring

For each inspection item, a score must be given to identify the urgency of required maintenance. The scoring is as follows:

0 = No deficiencies identified.

1 = Monitor – Although maintenance may not be required at this time, a potential problem exists that will most likely need to be addressed in the future. This can include items like minor erosion, concrete cracks/spalling, or minor sediment accumulation. This item should be revisited at the next inspection.

2 = Routine Maintenance Required – Some inspection items can be addressed through the routine maintenance program (See SOP in appendix C). This can include items like vegetation management or debris/trash removal.

3 = Immediate Repair Necessary – This item needs immediate attention because failure is imminent or has already occurred. This could include items such as structural failure of a feature (outlet works, forebay, etc), significant erosion, or significant sediment accumulation. This score should be given to an item that can significantly affect the function of the facility.

N/A This is checked by an item that may not exist in a facility. Not all facilities have all of the features identified on the form (forebay, micro-pool, etc.).

#### Inspection Summary/Additional Comments

Additional explanations to inspection items, and observations about the facility not covered by the form, are recorded in this section.

#### Overall Facility Rating

An overall rating must be given for each facility inspected. The overall facility rating should correspond with the highest score (0, 1, 2, 3) given to any feature on the inspection form.

C. Verification of Inspection and Form Submittal

The Stormwater Management Facility Inspection Form provides a record of inspection of the facility. Inspection Forms for each facility type are provided in Appendix D. Verification of the inspection of the stormwater facilities, the facility inspection form(s), and Inspector Qualifications shall be provided to the City of Aurora on an annual basis. The verification and the inspection form(s) shall be reviewed and submitted by <<Insert Property Owner’s Name>> or his/her property manager.

Refer to Section II of this Plan regarding the annual reporting of inspections.

1. Maintaining Stormwater Management Facilities  
   Stormwater management facilities shall be properly maintained to ensure they operate correctly, and provide the water quality treatment for which they were designed. Routine maintenance performed on a frequently scheduled basis, can help avoid more costly rehabilitative maintenance that results when facilities are not adequately maintained.

## A. Maintenance Categories

Stormwater management facility maintenance programs are separated into three broad categories of work. These categories are based largely on the Urban Drainage and Flood Control District’s Maintenance Program for regional drainage facilities. The categories are separated based upon the magnitude and type of the maintenance activities performed. A description of each category follows:

###### Routine Work

The majority of this work consists of scheduled mowings, trash and debris pickups for stormwater management facilities during the growing season. This includes items such as the removal of debris/material that may be clogging the outlet structure well screens and trash racks. It also includes activities such as weed control, mosquito treatment, and algae treatment. These activities normally will be performed numerous times during the year. It is the responsibility of the owner to clean all grates associated with the pond outlet structure after a storm event. These items can be completed without any prior correspondence with the City of Aurora; however, completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance activity with the annual report.

#### Restoration Work

This work consists of a variety of isolated or small-scale maintenance and work needed to address operational problems. Most of this work can be completed by a small crew, with minor tools, and small equipment. The <<Insert Property Owner’s Name>> shall correspond with the City of Aurora, and submit completed maintenance forms to the City of Aurora for each maintenance activity.

Rehabilitation Work

This work consists of large-scale maintenance and major improvements needed to address failures within the stormwater management facilities. This work requires consultation with the City of Aurora, and may require an engineering design with construction plans to be prepared for review and approval. This work may also require more specialized maintenance equipment, surveying, construction permits or assistance through private contractors and consultants. If these items are needed the <<Insert Property Owner’s Name>> shall correspond with the City of Aurora, and submit completed maintenance forms to the City of Aurora for each maintenance activity.

#### B.Maintenance Personnel

<<Insert Property Owner’s Name>> maintenance personnel shall be qualified to properly maintain stormwater management facilities. Inadequately trained personnel can cause additional problems resulting in additional maintenance costs.

C.Maintenance Forms

The Stormwater Management Facility Maintenance Form provides a record of maintenance activities. Maintenance Forms for each facility type are provided in Appendix E. Maintenance Forms shall be completed by the <<Insert Property Owner’s Name>> contractor completing the required maintenance items. The form shall then be reviewed by the <<Insert Property Owner’s Name>> or an authorized agent of the property owner and submitted on an annual basis to the City of Aurora.

Refer to Section II of this Plan regarding the annual reporting of inspections and maintenance activities performed.

**Appendix A**

**Stormwater Maintenance Agreement**

**Template**

Stormwater Maintenance Agreement between the City of Aurora, acting by and through its Utility Enterprise and

<<Insert Property Owner’s Name>> (Property Owner’s Name)

This Stormwater Maintenance Agreement (“Agreement”), effective \_\_\_\_\_\_\_\_\_\_\_\_, 20\_\_ is made by and between the City of Aurora (“City”), acting by and through its Utility Enterprise and <<Insert Property Owner’s Name>> ("Owner"). The City and Owner shall be referred to herein as “Party”, and collectively as “Parties”. The City and Owner agree as follows:

Paragraph 1. The Owner owns or will own certain property and public improvements, including stormwater and drainage improvements on the parcel of land known as Lot <<Insert Lot>>, Block <<Insert Block>>, <<Insert Subdivision>> Subdivision, Filing No.\_\_\_\_, County of <<Insert County>>, State of Colorado ("Property"). The Owner has installed, or caused to be installed, upon the Property the permanent stormwater Best Management Practices (BMPs). Certain inspections and maintenance of those BMPs are required under the Owner’s Inspection and Maintenance Plan, also referred to as the Operations and Maintenance Manual dated \_\_\_\_\_\_\_\_\_\_\_\_\_\_, 20\_\_ and approved by the City of Aurora (Inspection and Maintenance Plan (IM Plan)) which is attached, and made a part of this Stormwater Maintenance Agreement as Exhibit A. The Owner agrees, at the Owner's sole expense, to inspect, maintain, andto ensure proper functioning of the BMPs, in accord with and as set out in the IMPlan, as set forth herein below. If the Owner conveys the Property, Owner shall provide a copy of the IM Plan along with a copy of this Agreement to the Grantee. Upon conveyance, Owner shall thereafter be relieved of its obligations under this Agreement. However, such obligations shall run with the Property and become the obligation of Grantee.

Paragraph 2. In accordance with the City of Aurora Municipal Code 138-442.5**,** the Owner has submitted an IMPlan (Exhibit A). That IM Plan was approved by the City on \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, 20\_\_. The Owner has also submitted the Drainage Plan. That Drainage Plan was approved by the City on \_\_\_\_\_\_\_\_\_\_\_\_\_\_, 20\_\_.

Paragraph 3**.** The Owner shall inspect the BMPs at least once every calendar year, and shall submit written inspection reports to Aurora Water prior to May 31 of that calendar year. The City is under no obligation whatsoever pursuant to this Agreement to notify the Owner of any failure to submit inspection reports.

Paragraph 4. The Owner shall promptly perform all maintenance, and shall report maintenance activities to Aurora Water in accordance with the requirements set forth in the IM Plan.

Paragraph 5. Subject to the notice and Owner’s right to cure requirements of City of Aurora Municipal Code Section 138-442.5, in the event that the Owner fails to inspect, maintain, or repair any BMP, Owner agrees that the City, at the City's sole discretion, shall have the right to enter upon the Property without warrant or further process of law and may make whatever inspection. Following the City’s compliance with the notice requirements of 138-442.5, and Owner’s right to cure any deficiencies noted, if the Owner fails to timely cure such deficiencies, the City shall have the right to enter upon the Property without warrant or further process of law and may complete whatever maintenance or repair may be needed, all at the Owner's sole cost. The City shall bill the Owner by invoice for any costs incurred by the City, including but not limited to personnel, contracting, labor, or materials, and the Owner shall pay those costs within thirty (30) City business days of the invoice date.

Paragraph 6***.*** This Agreement shall be binding upon the Owner and the Owner's heirs, successors, and assigns. This Agreement shall be recorded at the Clerk and Recorder’s Office. The benefits and burdens of this Agreement shall run with the land.

Paragraph 7. Governing Law. This Agreement is subject to and shall be interpreted under the law of the State of Colorado, and the Charter, City Code, ordinances, rules, and regulations of the City of Aurora. The Parties agree that this Agreement shall be deemed to have been made in, and the place of performance is deemed to be in the City of Aurora, Colorado.

Paragraph 8. Appropriation and availability of funds. In accord with the Colorado Constitution, Article X, Section 20, and the City Charter, performance of the City's obligations under this Agreement is expressly subject to appropriation of funds by the City Council and the availability of those funds for expenditure.

Paragraph 9. No Third Party Beneficiary. It is expressly understood and agreed that enforcement of the terms and conditions of this Agreement, and all rights of action relating to such enforcement, shall be strictly reserved to the Parties hereto, and nothing contained in this Agreement shall give or allow any such claim or right of action by any other or third person or entity on this Agreement. It is the express intention of the Parties hereto that any person or entity, other than the Parties to this Agreement, receiving services or benefits under this Agreement shall be deemed to be incidental beneficiaries only.

Paragraph 10. Amendments. This Agreement may be amended only by prior writing executed by duly authorized representatives of the Property Owner and the City, and recorded in the records of the Clerk and Recorder's Office.

Paragraph 11. Headings. The headings of the several paragraphs of this Agreement are inserted only as a matter of convenience and for reference and do not define or limit the scope or intent of anyprovisions of this Agreement and shall not be construed to affect in any manner the terms and provisions hereof or the interpretation or construction thereof.

Paragraph 12. Entire Agreement. This Agreement, together with all exhibits attached hereto, constitutes the entire agreement between the Parties hereto, and all other representations or statements heretofore made, verbal or written, are merged herein, and this Agreement may be amended only in writing, and executed by duly authorized representatives of the Parties hereto.

Paragraph 13. Non-waiver of Rights. No waiver of default by the City of any of the terms, covenants, and conditions hereof to be performed, kept, and observed by the Owner shall be construed, or shall operate, as a waiver of any subsequent default of any of the terms, covenants, or conditions herein contained to be performed, kept, and observed by the Owner.

Paragraph 14. Waiver. This Agreement is for the benefit of the Owner. The Owner does hereby waive, remise, and release any claim, right, or cause of action the Owner may have or which may accrue in the future, whether under theories of contract or any other cause of action whatsoever, against the City arising in whole or in part from this Agreement.

City of Aurora, Colorado,

Acting by and through its

Utility Enterprise

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Vernon A. Adam Date

Engineering Services Manager

Approved as to form for Aurora:

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Ian Best, Assistant City Attorney Date

State of Colorado )

) ss

County of Arapahoe )

The foregoing instrument was acknowledged before me this \_\_\_\_\_ day of \_\_\_\_\_\_\_\_\_\_\_, 20\_\_, by Vernon A. Adam, Engineering Services Manager, acting on behalf of the Utility Enterprise of the City of Aurora, Colorado.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Acknowledgement

(For an individual acting in his or her own right)

For the Owner:

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing instrument was subscribed and affirmed before me this \_\_\_\_\_\_day of

\_\_\_\_\_\_\_\_, 20\_\_\_, by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

(The Acknowledgement (notarization) will vary for Owner depending on if Owner is an individual, corporation or partnership. Also, where there is mortgage on the property, the mortgage holder must sign the Subordination section of this Agreement.)

Acknowledgement

(For a Corporation)

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing instrument was subscribed and affirmed before me this \_\_\_\_\_day of \_\_\_\_\_\_\_\_\_\_\_\_, 20\_\_\_\_, by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, a \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ corporation, on behalf of the corporation.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Acknowledgement

(For a Partnership)

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_ \_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing instrument was subscribed and affirmed before me this \_\_\_\_\_\_day of \_\_\_\_\_\_\_\_, 20\_\_\_, by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, as \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, on behalf of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, a partnership.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Acknowledgement

(For an individual acting as principal by an attorney in fact)

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing instrument was subscribed and affirmed before me this \_\_\_\_\_\_day of \_\_\_\_\_\_\_\_, 20\_\_\_, by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, as an attorney in fact on behalf of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Acknowledgement

(By any public officer, trustee, or personal representative)

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing instrument was subscribed and affirmed before me this \_\_\_\_\_\_day of \_\_\_\_\_\_\_\_, 20\_\_\_, by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, as \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Subordination

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, as holder of a mortgage or other lien or interest described as \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_upon the parcel of land known as Lot \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, Block \_\_\_\_\_, \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Subdivision, Parcel Number \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_, hereby intentionally and unconditionally subordinates that mortgage or other lien or interest in favor of this Stormwater Maintenance Agreement.

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_

Print Name Signature Date

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Title

State of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

) ss

County of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ )

The foregoing Subordination was acknowledged before me this \_\_\_\_\_\_\_ day of \_\_\_\_\_\_\_\_\_\_, 20\_\_ by \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ as the Authorized Agent of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ on behalf of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_.

Witness my hand and official seal. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Notary Public

My commission expires: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Seal)

Exhibit A

Inspection and Maintenance Plan

**Appendix B**

**General Location and Description of Stormwater Management Facilities**

**Example**

**Appendix B**

## **General Location and Description of**

## **Stormwater Management Facilities**

**Example**

### General Site Description

*Insert General Site Description (example below****)***

Residential Site, Traditions Subdivision Filing No. 1, is located at the southeast corner of East 6th Avenue and Harvest Road approximately one mile east of Gun Club Road. The 81 acre site consists of 250 single-family residential units.

### General Stormwater Management Description

*Insert General Description of stormwater facilities for the site (example below****)***

All stormwater is conveyed via curb and gutter and conventional reinforced concrete pipe (RCP) storm sewer to one detention basin that provides detention and water quality treatment. The water quality facility is a constructed wetlands facility. Developed runoff is released at or below historic rates for the ten year, and 100 year storm events.

### Stormwater Facilities Site Plan

Inspection or maintenance personnel may utilize the Stormwater Facilities Map located in Appendix G for locating the stormwater facilities within this development.

### On-Site Stormwater Management Facilities

*List all facilities for each of the types (see examples provided below)* ***Volume Reduction Facilities***Residential Site utilizes Level I MDCIA – All impervious surfaces are routed over grass buffer strips. Gutter downspouts are disconnected from the storm conveyance system and are routed over grassed areas. ***Storage Facilities (Detention)***Detention for Residential Site is provided in a Detention Pond located at the southeast corner of East 6th Avenue and Harvest Road.   
 ***Water Quality Facilities***Residential Site utilizes one constructed wetlands basin for providing water quality capture volume for the site.   
 ***Source Control Best Management Practices***Residential Site does not include any nonstructural BMPs.

**Appendix C**

**Standard Operating Procedures for Extended Detention Basins (EDBs), Grass Buffers and Grass Swales (GB-GS), Bioretention Cell (BRCs) aka Porous Landscape Detention (PLDs), and Sand Filter Basins (SFBs)**

**Appendix C-1**

**Extended Detention Basins**

Standard Operation Procedures

for

Inspection and Maintenance

Extended Detention Basins

(EDBs)



June 2016**Table of Contents**

[EDB-1 Background 3](#_Toc168793065)

[EDB-2 Inspecting Extended Detention Basins (EDBs) 3](#_Toc168793066)

[EDB-2.1 Access and Easements 3](#_Toc168793067)

[EDB-2.2 Stormwater Management Facilities Locations 3](#_Toc168793068)

[EDB-2.3 Extended Detention Basin (EDB) Features 3](#_Toc168793069)

[EDB-2.3.1 Inflow Points 4](#_Toc168793070)

[EDB-2.3.2 Forebay 5](#_Toc168793071)

[EDB-2.3.3 Trickle Channel (Low-Flow) 6](#_Toc168793072)

[EDB-2.3.4 Bottom Stage 6](#_Toc168793073)

[EDB-2.3.5 Micropool 7](#_Toc168793074)

[EDB-2.3.6 Outlet Works 8](#_Toc168793075)

[EDB-2.3.7 Emergency Spillway 9](#_Toc168793076)

[EDB-2.3.8 Upper Stage (Dry Storage) 10](#_Toc168793077)

[EDB-2.3.9 Miscellaneous 11](#_Toc168793078)

[EDB-2.4 Inspection Forms 11](#_Toc168793079)

[EDB-3 Maintaining Extended Detention Basins (EDBS) 12](#_Toc168793080)

[EDB-3.1 Maintenance Personnel 12](#_Toc168793081)

[EDB-3.2 Equipment 12](#_Toc168793082)

[EDB-3.3 Safety 13](#_Toc168793083)

[EDB-3.4 Maintenance Forms 13](#_Toc168793084)

[EDB-3.5 Maintenance Categories and Activities 13](#_Toc168793085)

[EDB-3.6 Routine Maintenance Activities 13](#_Toc168793086)

[EDB-3.6.1 Mowing 14](#_Toc168793087)

[EDB-3.6.2 Trash/Debris Removal 14](#_Toc168793088)

[EDB-3.6.3 Outlet Works Cleaning 14](#_Toc168793089)

[EDB-3.6.4 Weed Control 15](#_Toc168793090)

[EDB-3.6.5 Mosquito/Algae Treatment 15](#_Toc168793091)

[EDB-3.7 Minor Maintenance Activities 15](#_Toc168793092)

[EDB-3.7.1 Sediment Removal 16](#_Toc168793094)

[EDB-3.7.2 Erosion Repair 16](#_Toc168793095)

[EDB-3.7.3 Vegetation Removal/Tree Thinning 16](#_Toc168793096)

[EDB-3.7.4 Clearing Drains/Jet-Vac 17](#_Toc168793097)

[EDB-3.8 Major Maintenance Activities 17](#_Toc168793098)

[EDB-3.8.1 Major Sediment Removal 17](#_Toc168793100)

[EDB-3.8.2 Major Erosion Repair 18](#_Toc168793101)

[EDB-3.8.3 Structural Repair 18](#_Toc168793102)

**EDB-1 Background**

Extended Detention Basins (EDBs) are one of the most common types of Stormwater Management Facilities utilized within the Front Range of Colorado. An EDB is a sedimentation basin designed to “extend” the runoff detention time, but to drain completely dry sometime after stormwater runoff ends. The EDB’s drain time for the water quality portion of the facility is typically forty (40) hours. The basins are considered to be “dry” because the majority of the basin is designed not to have a significant permanent pool of water remaining between runoff events.

EDBs are an adaptation of a detention basin used for flood control, with the primary difference is the addition of forebays, micro-pools and a slow release outlet design. Forebays are shallow concrete “pans” located at the inflow point to the basin and are provided to facilitate sediment removal within a contained area prior to releasing into the pond. These forebays collect and briefly hold stormwater runoff resulting in a process called sedimentation, dropping sediment out of the stormwater. The stormwater is then routed from the forebay into the concrete trickle channel and upper basin, the large grassy portion of the basin. The EDB uses a much smaller outlet that extends the emptying time of the more frequently occurring runoff events to facilitate pollutant removal. An EDB should have a small micro-pool just upstream of the outlet. This micro-pool is designed to hold a small amount of water to keep sediment and floatables from blocking the outlet orifices.

# **EDB-2 Inspecting Extended Detention Basins (EDBs)**

## **EDB-2.1 Access and Easements**

Inspection or maintenance personnel may utilize the stormwater facility map located in Appendix G containing the location(s) of the access points and maintenance easements of the EDB(s) within this development.

## **EDB-2.2 Stormwater Management Facilities Locations**

Inspection or maintenance personnel may utilize the stormwater facility map located in Appendix G containing the location(s) of the EDB(s) within this development.

## **EDB-2.3 Extended Detention Basin (EDB) Features**

EDBs have a number of features that are designed to serve a particular function. Many times the proper function of one feature depends on another. For example, if a forebay is not properly maintained, it could negatively affect the performance of a feature downstream (trickle channel, micro-pool, etc.). Therefore, it is critical that each feature of the EDB is properly inspected and maintained to ensure the overall facility functions as it was intended. Below is a list and description of the most common features within an EDB and the corresponding maintenance inspection items that can be anticipated:

**Table EDB-1**

**Typical Inspection and Maintenance Requirements Matrix**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **EDB Features** | **Sediment Removal** | **Mowing/Weed control** | **Trash & Debris Removal** | **Erosion** | **Overgrown Vegetation Removal** | **Standing Water (mosquito/algae control)** | **Structure Repair** |
| **Inflow Points (outfalls)** | X |  | X |  |  |  | X |
| **Forebay** | X |  | X |  |  |  | X |
| **Low-flow channel** | X |  | X | X | X |  | X |
| **Bottom Stage** | X | X | X | X | X | X |  |
| **Micro-pool** | X |  | X |  | X | X | X |
| **Outlet Works** | X |  | X |  |  |  | X |
| **Emergency Spillway** |  |  | X | X | X |  | X |
| **Upper Stage** |  |  | X | X |  |  |  |
| **Embankment** |  | X |  | X | X |  |  |

### EDB-2.3.1 Inflow Points

Inflow Points or Outfalls into EDBs are the point source of the stormwater discharge into the facility. An inflow point is commonly a storm sewer pipe with a flared end section that discharges into the EDB. In some instances, an inflow point could be a drainage channel or ditch that flows into the facility.

An energy dissipater (riprap or hard armor protection) is typically immediately downstream of the discharge point into the EDB to protect from erosion. In some cases, the storm sewer outfall can have a toe-wall or cut-off wall immediately below the structure to prevent undercutting of the outfall from erosion.

The typical maintenance items found with inflow points are as follows:

*a. Riprap Displaced* – Many times, because the repeated impact/force of water, the riprap can shift and settle. If any portion of the riprap apron appears to have settled, soil is present between the riprap, or the riprap has shifted, maintenance may be required to ensure future erosion is prevented. Depending on the nature of the maintenance the use of heavy equipment and proper bedding material may be required to repair the riprap. See Section EDB-3.5 – EDB-3.8.

*b. Erosion Present/Outfall Undercut* – In some situations, the energy dissipater may not have been sized, constructed, or maintained appropriately and erosion has occurred. Any erosion within the vicinity of the inflow point will require maintenance to prevent damage to the structure(s) and sediment transport within the facility. If there is any question to whether the original design is inadequate, a qualified engineer should review the situation to avoid chronic maintenance repairs if it is a design issue.

*c. Sediment Accumulation* – Because of the turbulence in the water created by the energy dissipater, sediment often deposits immediately downstream of the inflow point. To prevent a loss in hydraulic performance of the upstream infrastructure, sediment that accumulates in this area must be removed in a timely manner.

*d. Structural Damage* – Structural damage can occur at any time during the life of the facility. Typically, for an inflow, the structural damage occurs to the pipe flared end section (concrete or steel). Structural damage can lead to additional operating problems with the facility, including loss of hydraulic performance.

*e. Woody Growth/Weeds Present* – Undesirable vegetation can grow in and around the inflow area to an EDB that can significantly affect the performance of the drainage facilities discharging into the facility. This type of vegetation includes trees (typically cottonwoods) and dense areas of shrubs (willows). If woody vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate, resulting in blockage of the discharge. Also, tree roots can cause damage to the structural components of the inflow. Routine maintenance is essential for trees (removing a small tree/sapling is much cheaper and “quieter” than a mature tree). In addition, noxious weeds growing in the facility can result in the loss of desirable native vegetation and impact adjacent open spaces/land.

### EDB-2.3.2 Forebay

A forebay is a solid surface (pad), typically constructed of concrete, immediately downstream of the inflow point. The forebay is designed to capture larger particles and trash to prevent them from entering the main portion of the EDB. The solid surface is designed to facilitate mechanical sediment removal (skid steer). The forebay typically includes a small diameter discharge pipe or v-notch weir on the downstream end and designed to drain the forebay in a specified period of time to promote sedimentation. The forebays vary in size and depth depending on the design and site constraints.

*The typical maintenance items found with forebays are as follows:*

*a. Sediment/Debris Accumulation* – Because this feature of the EDB is designed to provide the initial sedimentation, debris and sediment frequently accumulate in this area. If the sediment and debris is not removed from the forebay on a regular basis, it can significantly affect the function of other features within the EDB. Routine sediment removal from the forebay can **significantly** reduce the need for dredging of the main portion of the EDB using specialized equipment (long reach excavators). Routine removal of sediment from the forebay can **substantially** decrease the long-term sediment removal costs of an EDB.

*b. Concrete Cracking/Failing* – The forebay is primarily constructed of concrete, which cracks, spalls, and settles. Damage to the forebay can result in deceased performance and impact maintenance efforts.

*c. Drain Pipe/Weir Clogged* – Many times the drainpipe or weir can be clogged with debris, and prevent the forebay from draining properly. If standing water is present in the forebay (and there is not a base flow), the forebay is most likely not draining properly. This can result in a decrease in performance and create potential nuisances with stagnant water (mosquitoes).

*d. Weir/Drain Pipe Damaged* – Routine maintenance activities, vandalism, or age may cause the weir or drain pipe in the forebay to become damaged. Weirs are typically constructed of concrete, which cracks and spalls. The drainpipe is typically smaller in diameter and constructed with plastic, which can fracture.

### EDB-2.3.3 Trickle Channel (Low-Flow)

The trickle channel conveys stormwater from the forebay to the micro-pool of the EDB. The trickle channel is typically made of concrete. However, grass lined (riprap sides protected) is also common and can provide for an additional means of water quality within the EDB. The trickle channel is typically six (6) to nine (9) inches in depth and can vary in width.

*The typical maintenance items found with trickle channels are as follows:*

*a. Sediment/Debris Accumulation* – Trickle channels are typically designed with a relatively flat slope that can promote sedimentation and the collection of debris. Also, if a trickle channel is grass lined it can accumulate sediment and debris at a much quicker rate. Routine removal of accumulated sediment and debris is essential in preventing flows from circumventing the trickle channel and affecting the dry storage portion of the pond.

*b. Concrete/Riprap Damage* – Concrete can crack, spall, and settle and must be repaired to ensure proper function of the trickle channel. Riprap can also shift over time and must be replaced/repaired as necessary.

*c. Woody Growth/Weeds Present* – Because of the constant moisture in the area surrounding the trickle channel, woody growth (cottonwoods/willows) can become a problem. Trees and dense shrub type vegetation can affect the capacity of the trickle channel and can allow flows to circumvent the feature.

*d. Erosion Outside of Channel* – In larger precipitation events, the trickle channel capacity will likely be exceeded. This can result in erosion immediately adjacent to the trickle channel and must be repaired to prevent further damage to the structural components of the EDB.

### EDB-2.3.4 Bottom Stage

The bottom stage is at least 1.0 to 2.0 feet deeper than the upper stage and is located in front of the outlet works structure. The bottom stage is designed to store the smaller runoff events, assists in keeping the majority of the basin bottom dry resulting in easier maintenance operations, and enhances the facilities pollutant removal capabilities. This area of the EDB may develop wetland vegetation.

*The typical maintenance items found with the bottom stage are as follows:*

*a. Sediment/Debris Accumulation* – The bottom stage can frequently accumulate sediment and debris. This material must be removed to maintain pond volume and proper function of the outlet structure.

*b. Woody Growth/Weeds Present* - Because of the constant moisture in the soil surrounding the micro-pool, woody growth (cottonwoods/willows) can create operational problems for the EDB. If woody vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate outside of the micro-pool (See EDB 2.3.5), which can cause problems with other EDB features. Also, tree roots can cause damage to the structural components of the outlet works. Routine management is essential for trees (removing a small tree/sapling is much cheaper and “quieter” than a mature tree).

*c. Bank Erosion* – The bottom stage is usually a couple feet deeper than the other areas of the ponds. Erosion can be caused by water dropping into the bottom stage if adequate protection/armor is not present. Erosion in this area must be mitigated to prevent sediment transport and other EDB feature damage.

*d. Mosquitoes/Algae Treatment* – Nuisance created by stagnant water can result from improper maintenance/treatment of the bottom stage. Mosquito larvae can be laid by adult mosquitoes within the permanent pool. Also, aquatic vegetation that grows in shallow pools of water can decompose causing foul odors. Chemical/mechanical treatment of the bottom stage may be necessary to reduce these impacts to adjacent homeowners.

*e. Petroleum/Chemical Sheen* – Many indicators of illicit discharges into the storm sewer systems will be present in the bottom stage area of the EDB. These indicators can include sheens, odors, discolored soil, and dead vegetation. If it is suspected that an illicit discharge has occurred, contact the supervisor immediately. Proper removal/mitigation of contaminated soils and water in the EDB is necessary to minimize any environmental impacts downstream.

### EDB-2.3.5 Micro-pool

The micro-pool is a concrete or grouted boulder walled structure directly in front of the outlet works. At a minimum, the micro-pool is 2.5 feet deep and is designed to hold water. The micro-pool is critical in the proper function of the EDB; it allows suspended sediment to be deposited at the bottom of the micro-pool and prevents these sediments from being deposited in front of the outlet works causing clogging of the outlet structure, which results in marshy areas within the top and bottom stages.

*The typical maintenance items found with micro-pools are as follows:*

*a. Sediment/Debris Accumulation* – The micro-pool can frequently accumulate sediment and debris. This material must be removed to maintain the micro pool volume, depth, and proper function of the outlet structure.

*b. Woody Growth/Weeds Present* - Because of the constant moisture in the soil surrounding the micro-pool, woody growth (cottonwoods/willows) can create operational problems for the EDB. If woody vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate outside of the micro-pool, which can cause problems with other EDB features. Also, tree roots can cause damage to the structural components of the outlet works. Routine management is essential for trees (removing a small tree/sapling is much cheaper and “quieter” than a mature tree).

*c. Mosquitoes/Algae Treatment* – Nuisance created by stagnant water can result from improper maintenance/treatment of the micro-pool. Mosquito larvae can be laid by adult mosquitoes within the permanent pool. If mosquitoes are breeding within the micro-pool this may also be an indication there is significant sediment build-up that is reducing the depth of the micro-pool. Also, aquatic vegetation that grows in shallow pools of water can decompose causing foul odors. Chemical/mechanical treatment of the micro-pool may be necessary to reduce these impacts to adjacent homeowners.

*d. Petroleum/Chemical Sheen* – Many indicators of illicit discharges into the storm sewer systems will be present in the micro-pool area of the EDB. These indicators can include sheens, odors, discolored soil, and dead vegetation. If it is suspected that an illicit discharge has occurred, contact the supervisor immediately. Proper removal/mitigation of contaminated soils and water in the EDB is necessary to minimize any environmental impacts downstream.

### EDB-2.3.6 Outlet Works

The outlet works is the feature that drains the EDB in specified quantities and periods of time. The outlet works is typically constructed of reinforced concrete into the embankment of the EDB. The concrete structure typically has steel orifice plates anchored/embedded into it to control stormwater release rates. The larger openings (flood control) on the outlet structure typically have trash racks over them to prevent clogging. The water quality orifice plate (smaller diameter holes) will typically have a well screen covering it to prevent smaller materials from clogging it. The outlet structure is the single most important feature in the EDB operation. Proper inspection and maintenance of the outlet works is essential in ensuring the long-term operation of the EDB.

*The typical maintenance items found with the outlet works are as follows:*

*a. Trash Rack/Well Screen Clogged* – Floatable material entering the EDB will most likely make its way to the outlet structure. This material is trapped against the trash racks and well screens on the outlet structure (which is why they are there). This material must be removed on a routine basis to ensure the outlet structure drains in the specified design period.

*b. Structural Damage* - The outlet structure is primarily constructed of concrete, which can crack, spall, and settle. The steel trash racks and well screens are also susceptible to damage.

*c. Orifice Plate Missing/Not Secure* – Many times residents, property owners, or maintenance personnel will remove or loosen orifice plates if they believe the pond is not draining properly. Any modification to the orifice plate(s) will significantly affect the designed discharge rates for water quality and/or flood control. Modification of the orifice plates is not allowed without approval from the City of Aurora Public Works Department, Engineering Control Division.

*d. Manhole Access* – Access to the outlet structure is necessary to properly inspect and maintain the facility. If access is difficult or not available to inspect the structure, chances are it will be difficult to maintain as well.

*e. Woody Growth/Weeds Present* - Because of the constant moisture in the soil surrounding the outlet works, woody growth (cottonwoods/willows) can create operational problems for the EDB. If woody vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate around the outlet works, which can cause problems with other EDB features. Also, tree roots can cause damage to the structural components of the outlet works. Routine management is essential for trees (removing a small tree/sapling is much cheaper and “quieter” than a mature tree).

### EDB-2.3.7 Emergency Spillway

An emergency spillway is typical of all EDBs and designed to serve as the overflow in the event the volume of the pond is exceeded. The emergency spillway is typically armored with riprap (or other hard armor) and is sometimes buried with soil. The emergency spillway is typically a weir (notch) in the pond embankment. Proper function of the emergency spillway is essential to ensure flooding does not affect adjacent properties.

*The typical maintenance items found with emergency spillways are as follows:*

*a. Riprap Displaced* – As mentioned before, the emergency spillway is typically armored with riprap to provide erosion protection. Over the life of an EDB, the riprap may shift or dislodge due to flow. Depending on the nature of the maintenance the use of heavy equipment and proper bedding material may be required to repair the riprap. See Section EDB-3.5 – EDB-3.8.

*b. Erosion Present* – Although the spillway is typically armored, stormwater flowing through the spillway can cause erosion damage. Erosion must be repaired to ensure the integrity of the basin embankment, and proper function of the spillway.

*c. Woody Growth/Weeds Present* – Management of woody vegetation is essential in the proper long-term function of the spillway. Larger trees or dense shrubs can capture larger debris entering the EDB and reduce the capacity of the spillway.

*d. Obstruction Debris* – The spillway must be cleared of any obstruction (man-made or natural) to ensure the proper design capacity.

### EDB-2.3.8 Upper Stage (Dry Storage)

The upper stage of the EDB provides the majority of the water quality flood detention volume. This area of the EDB is higher than the bottom stage and typically stays dry, except during storm events. The upper stage is the largest feature/area of the basin. Sometimes, the upper stage can be utilized for park space and other uses in larger EDBs. With proper maintenance of the bottom stage, micro-pool, and forebay(s), the upper stage should not experience much sedimentation; however, bottom elevations should be monitored to ensure adequate volume.

*The typical maintenance items found with upper stages are as follows:*

*a. Vegetation Sparse* – The upper basin is the most visible part of the EDB, and therefore aesthetics is important. Adequate and properly maintained vegetation can greatly increase the overall appearance and acceptance of the EDB by the public. In addition, vegetation can reduce the potential for erosion and subsequent sediment transport to the other areas of the pond.

*b. Woody Growth/Undesirable Vegetation* – Although some trees and woody vegetation may be acceptable in the upper basin, some thinning of cottonwoods and willows may be necessary. Remember, the basin will have to be dredged to ensure volume, and large trees and shrubs will be difficult to protect during that operation.

*c. Standing Water/Boggy Areas* – Standing water or boggy areas in the upper stage is typically a sign that some other feature in the pond is not functioning properly. Routine maintenance (mowing, trash removal, etc.) can be extremely difficult for the upper stage if the ground is saturated. If this inspection item is checked, make sure you have identified the root cause of the problem.

*d. Sediment Accumulation* – Although other features within the EDB are designed to capture sediment, the upper storage area will collect sediment over time. Excessive amounts of sedimentation will result in a loss of storage volume. It may be more difficult to determine if this area has accumulated sediment without conducting a field survey.

Below is a list of indicators:

1. Ground adjacent to the trickle channel appears to be several inches higher than the concrete/riprap trickle channel.
2. Standing water or boggy areas in upper stage.
3. Uneven grades or mounds.
4. Bottom Stage, Micro-pool, or Forebay has excessive amounts of sediment.

*e. Erosion (banks and bottom)* – The bottom grades of the dry storage area are typically flat enough that erosion should not occur. However, inadequate vegetative cover may result in erosion of the upper stage. Erosion that occurs in the upper stage can result in increased dredging/maintenance of the bottom stage/micro-pool.

*f. Trash/Debris* – Trash and debris can accumulate in the upper area after large events, or from illegal dumping. Over time, this material can accumulate and clog the EDB outlet works.

*g. Maintenance Access* – Most EDBs typically have a gravel/concrete maintenance access path to either the upper stage or forebay. This access path should be inspected to ensure the surface is still drivable. Some of the smaller EDBs may not have maintenance access paths; however, the inspector should verify that access is available from adjacent properties.

### EDB-2.3.9 Miscellaneous

There are a variety of inspection/maintenance issues that may not be attributed to a single feature within the EDB. This category on the inspection form is for maintenance items that are commonly found in the EDB, but may not be attributed to an individual feature.

*a. Encroachment in Easement Area* – Private lots/property can sometimes be located very close to the EDBs, even though they are required to be located in tracts with drainage easements. Property owners may not place landscaping, trash, fencing, or other items within the easement area that may adversely affect maintenance or the operation of the facility.

*b. Graffiti/Vandalism* – Damage to the EDB infrastructure can be caused by vandals. If criminal mischief is evident, the inspector should forward this information to the Aurora Police Department.

*c. Public Hazards* – Public hazards include items such as vertical drops of greater than four (4) feet, containers of unknown/suspicious substances, exposed metal/jagged concrete on structures. **If any hazard is found within the facility area that poses an immediate threat to public safety, call 911 immediately!**

*d. Burrowing Animals/Pests* – Prairie dogs and other burrowing rodents may cause damage to the EDB features and negatively affect the vegetation within the EDB.

*e. Other* – Any miscellaneous inspection/maintenance items not contained on the form should be entered here.

## 

## **EDB-2.4 Inspection Forms**

EDB Inspection forms are located in Appendix D. Inspection forms shall be completed by the person(s) conducting the inspection activities. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. These inspection forms shall be kept indefinitely and made available to the City of Aurora upon request.

# **EDB-3 Maintaining Extended Detention Basins (EDBS)**

## **EDB-3.1 Maintenance Personnel**

Maintenance personnel must be qualified to properly maintain EDBs. Inadequately trained personnel can cause additional problems resulting in additional maintenance costs.

## **EDB-3.2 Equipment**

It is imperative the appropriate equipment and tools are taken to the field with the operations crew. The types of equipment/tools will vary depending on the task at hand. Below is a basic list of tools, equipment, and material(s) that may be necessary to perform maintenance on an EDB:

1. Loppers/Tree Trimming Tools
2. Mowing Tractors
3. Trimmers (extra string)
4. Shovels
5. Rakes
6. All Surface Vehicle (ASVs)
7. Skid Steer
8. Back Hoe
9. Track Hoe/Long Reach Excavator
10. Dump Truck
11. Jet-Vac Machine
12. Engineers Level (laser)
13. Riprap (Minimum - Type M, or as shown on the approved civil plans)
14. Filter Fabric
15. Erosion Control Blanket(s)
16. Seed Mix (See seed mix in the *Rules and Regulations Regarding Stormwater (Quality) Discharge for Construction Activities*, Std Det. SM, Seeding & Mulching)
17. Illicit Discharge Cleanup Kits
18. Trash Bags
19. Tools (wrenches, screw drivers, hammers, etc)
20. Chain Saw
21. Confined Space Entry Equipment
22. Approved Stormwater Facility Inspection and Maintenance Plan

Some of the items identified above may not be needed for every maintenance operation. However, this equipment should be available to the maintenance operations crews should the need arise.

## **EDB-3.3 Safety**

Vertical drops may be encountered in areas located within and around the facility. Avoid walking on top of retaining walls or other structures having a significant vertical drop. If a vertical drop within the EDB is identified as greater than 48” in height, make the appropriate note/comment on the maintenance inspection form.

## **EDB-3.4 Maintenance Forms**

The EDB Maintenance Form provides a record of each maintenance operation performed by maintenance contractors. The EBD Maintenance Form shall be filled out in the field after the completion of the maintenance operation. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. The EDB Maintenance form is located in Appendix E.

## **EDB-3.5 Maintenance Categories and Activities**

A typical EDB Maintenance Program will consist of three broad categories of work. Within each category of work, a variety of maintenance activities can be performed on an EDB. A maintenance activity can be specific to each feature within the EDB, or general to the overall facility. This section of the SOP explains each of the categories and briefly describes the typical maintenance activities for an EDB.

A variety of maintenance activities are typical of EDBs. The maintenance activities range in magnitude from routine trash pickup to the reconstruction of drainage infrastructure. Below is a description of each maintenance activity, the objectives, and frequency of actions:

## **EDB-3.6 Routine Maintenance Activities**

The majority of this work consists of regularly scheduled mowing and trash and debris pickups for stormwater management facilities during the growing season. This includes items such as the removal of debris/material that may be clogging the outlet structure well screens and trash racks. It also includes activities such as weed control, mosquito treatment, and algae treatment. These activities normally will be performed numerous times during the year. These items can be completed without any prior correspondence with the City of Aurora; however, completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance activity in accordance with the Inspection and Maintenance Plan.

The Maintenance Activities are summarized below, and further described in the following sections.

**Table – EDB-2**

**Summary of Routine Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| Mowing | Twice annually | Excessive grass height/aesthetics | Mow grass to a height of 4” to 6” |
| **Trash/Debris Removal** | Twice annually | Trash & debris in EDB | Remove and dispose of trash and debris |
| **Outlet Works Cleaning** | As needed - after significant rain events – twice annually min. | Clogged outlet structure; ponding water | Remove and dispose of debris/trash/sediment to allow outlet to function properly |
| **Weed control** | Minimum twice annually | Noxious weeds; Unwanted vegetation | Treat w/ herbicide or hand pull; Consult the local weed specialist |
| **Mosquito Treatment** | As needed | Standing water/mosquito habitat | Treat w/ EPA approved chemicals |
| **Algae Treatment** | As needed | Standing water/ Algal growth/green color | Treat w/ EPA approved chemicals |

### EDB-3.6.1 Mowing

Occasional mowing is necessary to limit unwanted vegetation and to improve the overall appearance of the EDB. Native vegetation should be mowed to a height of four (4) to six (6) inches tall. Grass clippings should be collected and disposed of properly.

*Frequency* – Routine - Minimum of twice annually or depending on aesthetics.

### EDB-3.6.2 Trash/Debris Removal

Trash and debris must be removed from the entire EDB area to minimize outlet clogging and to improve aesthetics. This activity must be performed prior to mowing operations.

*Frequency –* Routine – Prior to mowing operations and minimum of twice annually and should be done after significant storm events.

### EDB-3.6.3 Outlet Works Cleaning

Debris and other materials can clog the outlet work’s well screen, orifice plate(s) and trash rack. This activity must be performed anytime other maintenance activities are conducted to ensure proper operation.

*Frequency* - Routine – After significant rainfall event or concurrently with other maintenance activities.

### EDB-3.6.4 Weed Control

Noxious weeds and other unwanted vegetation must be treated as needed throughout the EDB. This activity can be performed either through mechanical means (mowing/pulling) or with herbicide. Consultation with the local Weed Inspector is highly recommended prior to the use of an herbicide. All herbicide applications should be applied in accordance with the manufacturer’s recommendations.

*Frequency –* Routine – As needed based on inspections.

### EDB-3.6.5 Mosquito/Algae Treatment

Treatment of permanent pools is necessary to control mosquitoes and undesirable aquatic vegetation that can create nuisances. Only EPA approved chemicals/materials can be used in areas that are warranted.

*Frequency* – As needed.

### EDB- 3.7 Minor Maintenance Activities

#### This work consists of a variety of isolated or small-scale maintenance or operational problems. Most of this work can be completed by a small crew, tools, and small equipment. These items require prior correspondence with the City of Aurora Water Staff, and require completed inspection and maintenance forms to be submitted to the City of Aurora Water Staff for each inspection and maintenance activity.

**Table – EDB-3**

### Summary of Minor Maintenance Activities

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| Sediment Removal\* | As needed; typically every 1–2 years | Sediment build-up; decrease in pond volume | Remove and dispose of sediment |
| **Erosion Repair** | As needed, based upon inspection | Rills/gullies forming on side slopes, trickle channel, other areas | Repair eroded areas  Revegetate; address source of erosion |
| **Vegetation Removal/Tree Thinning** | As needed, based upon inspection | Large trees/wood vegetation in lower chamber of pond | Remove vegetation; restore grade and surface |
| **Drain Cleaning/Jet Vac** | As needed, based upon inspection | Sediment build-up /non draining system | Clean drains; Jet Vac if needed |

\*Usually from the forebay, trickle channel, and/or micro-pool

### EDB-3.7.1 Sediment Removal

Sediment removal is necessary to maintain the original design volume of the EDB and to ensure proper function of the infrastructure. Regular sediment removal (minor) from the forebay, inflow(s), and trickle channel can significantly reduce the frequency of major sediment removal activities (dredging) in the upper and lower stages. The minor sediment removal activities can typically be addressed with shovels and smaller equipment.

Stormwater sediments removed from EDBs do not meet the criteria of “hazardous waste”. However, these sediments are contaminated with a wide array of organic and inorganic pollutants and handling must be done with care. Sediments from permanent pools must be carefully removed to minimize turbidity, further sedimentation, or other adverse water quality impacts. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a landfill for proper disposal. Prompt and thorough cleanup is important should a spill occur during transportation.

*Frequency* – Non-routine – As necessary based upon inspections. Sediment removal in the forebay, trickle channel, and micro-pool may be necessary as frequently as every 1-2 years.

### EDB-3.7.2 Erosion Repair

The repair of eroded areas is necessary to ensure the proper function of the EDB, minimize sediment transport, and to reduce potential impacts to other features. Erosion can vary in magnitude from minor repairs to trickle channels, energy dissipaters, and rilling to major gullies in the embankments and spillways. The repair of eroded areas may require the use of excavators, earthmoving equipment, riprap, concrete, erosion control blankets, and turf reinforcement mats. Major erosion repair to the pond embankments, spillways, and adjacent to structures will require consultation with the City of Aurora Water, and Engineering Staff.

*Frequency* – Non-routine – As necessary based upon inspections.

### EDB-3.7.3 Vegetation Removal/Tree Thinning

Dense stands of woody vegetation (willows, shrubs, etc) or trees can create maintenance problems for the infrastructure within an EDB. Tree roots can damage structures and invade pipes/channels thereby blocking flows. Also, trees growing in the upper and lower stages of the EDB will most likely have to be removed when sediment/dredging operations occur. A small tree is easier to remove than a large tree, therefore, regular removal/thinning is imperative. All trees and woody vegetation that is growing in the bottom of the EDB or near structures (inflows, trickle channels, outlet works, emergency spillways, etc.) should be removed. Any trees or woody vegetation in the EDB should be limited to the upper portions of the pond banks.

*Frequency –* Non-routine – As necessary based upon inspections.

### EDB-3.7.4 Clearing Drains/Jet-Vac

An EDB contains many structures, openings, and pipes that can be frequently clogged with debris. These blockages can result in a decrease of hydraulic capacity and create standing water in areas outside of the micro-pool. Many times the blockage to this infrastructure can be difficult to access and/or clean. Specialized equipment (jet-vac machines) may be necessary to clear debris from these difficult areas.

*Frequency –* Non-routine – As necessary based upon inspections.

## **EDB-3.8 Major Maintenance Activities**

This work consists of larger maintenance/operational problems and failures within the stormwater management facilities. All of this work requires consultation with the City of Aurora to ensure the proper maintenance is performed. This work requires the City of Aurora Water Staff review the original design before approval of the proposed maintenance. **A public improvements permit shall be required for all major maintenance activities.** This work may also require more specialized maintenance equipment, design/details, submittal of plans to the City of Aurora for review and approval, surveying, or assistance through private contractors and consultants.

**Table – EDB-4**

### Summary of Major Maintenance Activities

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Major Sediment Removal** | As needed – based upon scheduled inspections | Large quantities of sediment; reduced pond capacity | Remove and dispose of sediment. Repair vegetation as needed |
| **Major Erosion Repair** | As needed – based upon scheduled inspections | Severe erosion including gullies, excessive soil displacement, areas of settlement, holes | Repair erosion – find cause of problem and address to avoid future erosion |
| **Structural Repair** | As needed – based upon scheduled inspections | Deterioration and/or damage to structural components – broken concrete, damaged pipes, outlet works | Structural repair to restore the structure to its original design |

### EDB-3.8.1 Major Sediment Removal

Major sediment removal consists of removal of large quantities of sediment or removal of sediment from vegetated areas. Care shall be given when removing large quantities of sediment and sediment deposited in vegetated areas. Large quantities of sediment need to be carefully removed, transported and disposed of. Vegetated areas need special care to ensure design volumes and grades are preserved.

Major sediment removal activities will require larger and more specialized equipment. The major sediment activities will also require surveying with an engineer’s level, and consultation with the City of Aurora Water, and Engineering Staff to ensure design volumes/grades are achieved. Pond volume recertification will be required in accordance with the City of Aurora’s drainage criteria manual.

*Frequency* – Non-routine – Repair as needed based upon inspections.

### EDB-3.8.2 Major Erosion Repair

Major erosion repair consists of filling and revegetating areas of severe erosion. Determining the cause of the erosion as well as correcting the condition that caused the erosion should also be part of the erosion repair. Care should be given to ensure design grades and volumes are preserved. Any condition/repair affecting design grades or pond volumes requires consultation with the City of Aurora Water and Engineering Staff.

*Frequency* – Non-routine – Repair as needed based upon inspections.

### EDB-3.8.3 Structural Repair

An EDB includes a variety of structures that can deteriorate or be damaged during the course of use and routine maintenance. These structures are constructed of steel and concrete that can degrade or be damaged and may need to be repaired or re-constructed from time to time. These structures include items like outlet works, trickle channels, forebays, inflows and other features. In-house operations staff can perform some of the minor structural repairs. Major repairs to structures may require input from a structural engineer and specialized contractors. Consultation with the City of Aurora, and Engineering Staff shall take place prior to all structural repairs.

*Frequency* – Non-routine – Repair as needed based upon inspections.

Reference:

**This plan is adapted from Southeast Metro Stormwater Authority,** *Operation and Maintenance (O & M) Manual,* **and Town of Parker, Colorado,** *Stormwater Permanent Best Management Practices (PBMP) Long-Term Operation and Maintenance Manual*, October 2004

**Appendix C-2**

**Grass Buffers and Grass Swales**

Standard Operation Procedures

for

Inspection and Maintenance

Grass Buffers and Grass Swales

(GB-GS)



September 2010

**Table of Contents**

[**GB-GS-1** **Background** 3](#_Toc182883068)

[**GB-GS-2 Inspecting Grass Buffers and Swales (GB-GS) 3**](#_Toc182883069)

[GB-GS-2.1 Access and Easements 3](#_Toc182883070)

[GB-GS-2.2 Stormwater Management Facilities Locations 3](#_Toc182883071)

[GB-GS-2.3 Grass Buffer - Grass Swale (GB-GS) Features 3](#_Toc182883072)

[GB-GS-2.3.1 Grass Swale Bottom and Side Slopes; Grass Buffer Strips 4](#_Toc182883073)

[GB-GS-2.3.2 Inflow Points 5](#_Toc182883074)

[GB-GS-2.3.3 Underdrain System 5](#_Toc182883075)

[GB-GS-2.3.4 Grade Control Level Spreader 6](#_Toc182883076)

[GB-GS-2.3.5 Irrigation 6](#_Toc182883077)

[GB-GS-2.3.6 Miscellaneous 6](#_Toc182883078)

[GB-GS-2.4 Inspection Forms 7](#_Toc182883079)

[**GB-GS-3 Maintaining Grass Buffers and Grass Swales (GB-GS) 7**](#_Toc182883080)

[GB-GS-3.1 Maintenance Personnel 7](#_Toc182883081)

[GB-GS-3.2 Equipment 7](#_Toc182883082)

[GB-GS-3.3 Maintenance Forms 8](#_Toc182883083)

[GB-GS-3.4 Maintenance Categories and Activities 8](#_Toc182883084)

[GB-GS-3.5 Routine Maintenance Activities 8](#_Toc182883085)

[GB-GS-3.5.1 Trash/Debris Removal 9](#_Toc182883086)

[GB-GS-3.5.2 Mowing 9](#_Toc182883087)

[GB-GS-3.5.3 Irrigation 10](#_Toc182883088)

[GB-GS-3.5.4 Weed Control 10](#_Toc182883089)

[GB-GS-3.5.5 Mosquito Treatment 10](#_Toc182883090)

[GB-GS-3.5.6 Level Spreader (Grass Buffer only) 10](#_Toc182883091)

[GB-GS-3.5.7 Rodent Damage 11](#_Toc182883092)

[GB-GS-3.6 Minor Maintenance Activities 11](#_Toc182883093)

[GB-GS-3.6.1 Sediment Removal 11](#_Toc182883094)

[GB-GS-3.6.2 Erosion Repair 12](#_Toc182883095)

[GB-GS-3.6.3 Vegetation Removal 12](#_Toc182883096)

[GB-GS-3.6.4 Revegetation 12](#_Toc182883097)

[GB-GS-3.6.5 Irrigation (Automatic) 12](#_Toc182883098)

[GB-GS-3.6.6 Level Spreader 12](#_Toc182883099)

[GB-GS-3.6.7 Fertilization/Soil Amendment 13](#_Toc182883100)

[GB-GS-3.6.8 Vehicle Tracks 13](#_Toc182883101)

[GB-GB-3.7 Major Maintenance Activities 13](#_Toc182883102)

[GB-GS-3.7.1 Major Sediment/Pollutant Removal 14](#_Toc182883103)

[GB-GS-3.7.2 Major Erosion Repair 15](#_Toc182883104)

[GB-GS-3.7.3 Structural Repair 15](#_Toc182883105)

[GB-GS-3.7.4 GB-GS Rebuild 15](#_Toc182883106)

GB-GS-1 Background

Grass Buffers and Grass Swales are common types of Stormwater Management Facilities utilized within the Front Range of Colorado. Grass Buffers and Grass Swales promote filtration, infiltration, and settling to reduce runoff volume.

Grass Buffers are uniformly graded and densely vegetated areas of turf grass. They are designed to accommodate sheet flow rather than concentrated or channelized flow. They are typically located adjacent to impervious areas such as parking lots or along roads. Grass Buffers are designed to evenly distribute runoff across the width of the buffer to achieve uniform sheet-flow conditions. A flow spreader may be incorporated for this purpose. In some cases, grass buffers may have underdrain systems.

Grass Swales are densely vegetated drainage ways with low-pitched side slopes that collect and convey runoff. Design of their longitudinal slope and cross section forces the flow to be slow and shallow, thereby facilitating sedimentation while limiting erosion. Berms or check dams may be installed perpendicular to the flow to decrease the slope and slow down the flow. Grass swales are used in open space and landscaped areas to collect and convey overland flows, and can be used as an alternative to curb and gutter (when approved by the City Engineer) to collect and convey street flows. Some grass swales are designed with underdrain systems.

# **GB-GS-2 Inspecting Grass Buffers and Swales (GB-GS)**

## **GB-GS-2.1 Access and Easements**

Inspection and maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the access points and maintenance easements of the GB-GSs within this development.

## **GB-GS-2.2 Stormwater Management Facilities Locations**

Inspection and maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the GB-GSs within this development.

## **GB-GS-2.3 Grass Buffer - Grass Swale (GB-GS) Features**

GB-GSs are unique stormwater quality facilities, in that they are typically viewed as landscaping or ground cover, and are often overlooked as water quality treatment facilities. GB-GSs have a number of features designed to serve a particular function. It is important for maintenance personnel to understand the function of each of these features. Below is a list of the common features of a Grass Swale or Grass Buffer and the corresponding maintenance inspection items anticipated:

**Table GB-GS-1**

**Typical Inspection & Maintenance Requirements Matrix**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | **Sediment Removal** | **Mowing**  **Weed control** | **Trash & Debris Removal** | **Erosion** | **Removal/ Replacement** | **Structural Repair** |
| Swale Bottom | X | X | X | X |  |  |
| **Side Slope** |  | X | X | X |  |  |
| **Buffer Strip** | X | X | X | X |  |  |
| **Inflows** | X | X | X | X | X | X |
| **Underdrain System\*** |  |  |  |  | X |  |
| **Grade Control/Level Spreader** |  |  |  | X |  | X |
| **Irrigation System** |  |  |  |  | X |  |

\*If the design and inspection allows, flushing of the system may be all that is needed.

### GB-GS-2.3.1 Grass Swale Bottom and Side Slopes; Grass Buffer Strips

Grass Swales and Grass Buffers require general maintenance of the turf grass and repair of any rill or gully development. The bottom and side slopes of grass swales and the area of grass buffer strips should be maintained with dense vegetative cover, and should not be eroded or bare. Inspection over the first few years will help to determine if any problems are developing.

The typical maintenance items required at the side slopes and bottoms of grass swales and within grass buffer areas are as follows:

*a. Sediment Accumulation* – The purpose of the grass swale or buffer is to slow down flow and allow sedimentation to occur. To prevent a loss in performance of the swale or buffer, sediment that accumulates must be removed on a timely basis.

*b. Vegetation Sparse* – Grass Swales and Buffers rely on a healthy, dense cover of grass to decrease the flow velocities and promote sedimentation and infiltration. Grasses that are diseased, dying or otherwise damaged should be replaced. All bare areas should be reseeded or patched. Causes which contribute to the damaged grass cover, including lack of adequate irrigation, traces of pedestrian or vehicular traffic, uncontrolled weeds, excessive sedimentation accumulation, etc., should be identified and remedied.

*c. Erosion Present* – Lack of adequate vegetative cover or excessive flow velocities may result in rill or gully development, and erosion of the swale or buffer strip. Erosion will require maintenance to prevent further damage to the area and to prevent sediment transport.

d. *Standing Water/Boggy Areas* – Grass swales and buffers are generally intended to drain and be dry in between rain events. If areas of standing water are present, the swale or buffer may need to be evaluated for proper grade to ensure drainage or the addition of underdrains. In some cases, where underdrains are used, the underdrains should be inspected to ensure that they are not clogged.

### GB-GS-2.3.2 Inflow Points

Inflow points are the points of stormwater discharge into the swale or buffer. Inflow points are typically pipe outfalls, other grass swales or buffers, or curb cuts from upstream impervious areas, such as parking lots. Some form of energy dissipation is typically provided immediately downstream of the inflow point into the grass swale or buffer. Energy dissipation devices may include riprap aprons, or flow spreader devices.

The typical maintenance items required at inflow points are as follows:

*a. Riprap Displaced/Rundown Damaged* – Often, because of, the repeated impact/force of water, the riprap can shift and settle. If any portion of the riprap rundown or apron appears to have settled, if soil is present between the riprap, or if the riprap has shifted, maintenance may be required to ensure future erosion is prevented.

*b. Erosion Present/Outfall Undercut* – In some situations, an energy dissipater may have not been provided, or may not have been sized, constructed, or maintained appropriately and erosion has occurred. Any erosion within the vicinity of the inflow point will require maintenance to prevent damage to the structure(s) and sediment transport within the facility.

*c. Sediment Accumulation* – Because of the turbulence in the water created by the energy dissipater, sediment often deposits immediately downstream of the inflow point. To prevent a loss in performance, sediment that accumulates in this area must be removed on a timely basis.

### GB-GS-2.3.3 Underdrain System

Some grass swales and buffers that have a flatter slope or soils which do not allow adequate percolation or are in areas with a continuous base flow may have been installed with an underdrain system. Underdrains typically consist of a layer of geotextile fabric, gravel storage area and perforated PVC pipe. The geotextile fabric is utilized to prevent the filter material from entering the underdrain system. The gravel storage area allows for storage of treated stormwater runoff prior to the discharge of the runoff through the perforated PVC pipe.

*The typical maintenance activities required for the underdrain system are as follows:*

With proper maintenance of the grassed areas, there should be a minimum amount of maintenance required on the underdrain system. Generally the only maintenance performed on the underdrain system is jet-vac cleaning in the event it becomes clogged.

### GB-GS-2.3.4 Grade Control Level Spreader

Grass swales installed in areas with steep longitudinal slopes often necessitate the use of grade control checks or drop structures. Grade control structures are typically either concrete walls or rip rap structures that serve to provide a reinforced drop at specific locations in the channel, reducing the longitudinal slope between the control structures.

Level Spreaders are installed on the upstream of grass buffers to evenly distribute flows along the design length. Level spreaders may consist of slotted curbing, modular block porous pavement, level walls or other spreader devices.

*The typical maintenance activities required for grade control structures and level spreaders are as follows:*

*a. Erosion present* – Grade control structures and level spreaders are provided to reduce the potential for erosion of the grassed swale or buffer areas. Erosion within the vicinity of the control structure or level spreader indicates the structure is not functioning as intended and requires maintenance to prevent future erosion and damage. Or, review the original design if erosion becomes chronic.

*b. Structural damage* – Structural damage can occur at any time along the life of the facility. Typically, structural damage occurs with the deterioration of concrete, including cracking, spalling or settling and the erosion and deterioration of the riprap structures. Level spreaders may settle unevenly creating low areas, which concentrate the flows. Partial or full replacement may be required depending on the extent of the damage.

### GB-GS-2.3.5 Irrigation

Grass Buffers and Grass Swales depend on healthy, dense turf grass to function, and therefore require an irrigation system, to provide a consistent water supply. Typically, the condition of the grass cover will provide evidence of the effectiveness and maintenance needs of the irrigation system.

*The typical maintenance activities required for irrigation systems are as follows:*

Irrigation systems will generally require routine periodic maintenance and adjustment to ensure proper amounts of water are being applied given the weather conditions, and that they are providing coverage to all areas of the grass to eliminate bare spots.

### GB-GS-2.3.6 Miscellaneous

There are a variety of inspection/maintenance issues that may not be attributed to a single feature within the GB-GS. This category on the inspection form is for maintenance items commonly found in the GB-GS, but may not be attributed to an individual feature.

*a. Encroachment in Easement Area* – The City of Aurora requires GB-GS be located in tracts or drainage easements. Property owners may not place landscaping, trash, fencing, or other items within the easement area that may adversely affect maintenance or the operation of the facility.

*b. Public Hazards* – Public hazards include items such as containers of unknown/suspicious substances, and exposed metal/jagged concrete on structures. **If any unknown/suspicious hazard is found within the facility area that poses an immediate threat to public safety, call 911 immediately.**

*c. Burrowing Animals/Pests*– Prairie dogs and other burrowing rodents may cause damage to the GB-GS features and negatively affect the vegetation within the GB-GS.

*d. Other* – Any miscellaneous inspection/maintenance items not contained on the form should be entered here.

## **GB-GS-2.4 Inspection Forms**

GB-GS Inspection forms are located in Appendix D. Inspection forms shall be completed by the person(s) conducting the inspection activities. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. These inspection forms shall be kept indefinitely and made available to the City of Aurora upon request

# **GB-GS-3 Maintaining Grass Buffers and Grass Swales (GB-GS)**

## **GB-GS-3.1 Maintenance Personnel**

Maintenance personnel must be experienced to properly maintain GB-GSs. Inadequately trained personnel can cause additional problems resulting in additional maintenance costs.

GB-GS-3.2 Equipment

It is imperative the appropriate equipment and tools are taken to the field with the operations crew. The types of equipment/tools will vary depending on the task at hand. Below is a basic list of tools, equipment, and material(s) that may be necessary to perform maintenance on a GB-GS:

1. Mowing Tractors
2. Trimmers (extra string)
3. Shovels
4. Rakes
5. All Surface Vehicle (ASVs)
6. Engineers Level (laser)
7. Erosion Control Blanket(s)
8. Mulch
9. Sod or Seed (See seed mix in the *Rules and Regulations Regarding Stormwater (Quality) Discharge for Construction Activities*, Std Det. SM, Seeding & Mulching)
10. Illicit Discharge Cleanup Kits
11. Trash Bags
12. Jet-Vac Equipment
13. Stormwater Facility Inspection and Maintenance Plan

Some of the items identified above may not be needed for every maintenance operation. However, this equipment should be available to the maintenance operations crews should the need arise.

## **GB-GS-3.3 Maintenance Forms**

The GB-GS Maintenance Form provides a record of each maintenance operation performed by maintenance contractors. The GB-GS Maintenance Form shall be filled out in the field after the completion of the maintenance operation. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. The GB-GS Maintenance form is located in Appendix E.

## **GB-GS-3.4 Maintenance Categories and Activities**

A typical GB-GS Maintenance Program will consist of three broad categories of work: Routine, Minor and Major. Within each category of work, a variety of maintenance activities can be performed on a GB-GS. A maintenance activity can be specific to each feature within the GB-GS, or general to the overall facility. This section of the SOP explains each of the categories and briefly describes the typical maintenance activities for a GB-GS.

A variety of maintenance activities are typical of GB-GSs. The maintenance activities range in magnitude from routine trash pickup to the reconstruction of the GB-GS or underdrain system. Below is a description of each maintenance activity, the objectives, and frequency of actions.

## **GB-GS-3.5 Routine Maintenance Activities**

The majority of this work consists of scheduled mowing, trash and debris pickups and landscape care for the GB-GS during the growing season. It also includes activities such as weed control. These activities normally will be performed numerous times during the year. These items do notrequire any prior approval by the City of Aurora, however, completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance activity in accordance with the Inspection and Maintenance plan.

The Routine Maintenance Activities are summarized below, and further described in the following sections.

**Table GB-GS-2**

**Summary of Routine Maintenance Activities**

| **Maintenance Activity** | **Minimum Frequency** | **Indication Action is Needed:** | **Maintenance Action** |
| --- | --- | --- | --- |
|  |  |  |  |
| **Trash/Debris Removal** | Twice annual and before mowing | Trash & debris in GB-GS | Remove and properly dispose of trash and debris |
| **Mowing** | Routine – as necessary to maintain 2”- 4” grass height | Excessive grass height/aesthetics | 2”- 4” grass height for turf grass; 4” - 6” for native grass |
| **Irrigation (Automatic)** | Three times annually | Areas of insufficient or excess watering; broken or missing parts | SPRING: start up system; test for even coverage and correct timer settings  SUMMER: test for even coverage and correct timer settings  FALL: drain and winterized system  (follow watering regulations) |
| **Irrigation**  **(Not Automatic)** | As needed to maintain healthy grass | Areas of insufficient or excess watering | Water as needed to maintain healthy grass; (follow watering regulations) |
| **Weed Control** | Minimum twice annually | Noxious weeds; Unwanted vegetation | Treat w/herbicide or hand pull; consult a local Weed Inspector |
| **Mosquito Treatment** | As needed, based upon inspections | Standing water/  mosquito habitat | Perform maintenance to eliminate standing water\*; Treat w/ EPA approved chemicals |
| **Level Spreader**  **(Grass Buffer only)** | As needed, based upon inspections | Evidence of uneven flow/localized erosion | Look for cause; repair, fill or revegetate areas of erosion |
| **Rodent Damage** | As needed, based upon inspections | Holes, small piles of dirt, raised burrows | Evaluate damage; contact Parks Dept. or Division of Wildlife for guidance |

\*See Section GB-GS-2.3.1d for further discussion

### GB-GS-3.5.1 Trash/Debris Removal

Trash and debris must be removed from the GB-GS area to allow for proper functioning and to improve aesthetics. This activity must be performed prior to mowing operations.

*Frequency –* Routine – Prior to mowing operations and a minimum of twice annually.

### GB-GS-3.5.2 Mowing

Routine mowing of the turf grass embankments is necessary to maintain an appropriate grass height and to improve the overall appearance of the GB-GS. Turf grass should be mowed to a height of 2 to 4 inches (4-6 inches for native grass) and shall be bagged to prevent potential contamination of the filter media, especially if there is an underdrain system.

*Frequency* – Routine – as necessary to maintain grass height.

### GB-GS-3.5.3 Irrigation

Irrigation systems should be maintained in proper working order to provide an adequate water supply to support the grass cover. When automatic irrigation systems are not available, alternate methods for providing a water supply during times of drought must be provided.

Automatic irrigation systems should be maintained routinely throughout the growing season to ensure that they are providing the appropriate amounts of water, and are providing complete coverage of the area. Sprinkler heads should be adjusted as necessary, and checked for broken or missing parts.

*Frequency -* Routine as needed throughout the growing season, plus the following:

Spring: Start up the system and test for even coverage and correct timer settings.

Summer: Test for even coverage and correct timer settings.

Fall: Drain and winterize the system.

### GB-GS-3.5.4 Weed Control

Noxious weeds and other unwanted vegetation must be treated as needed throughout the GB-GS. This activity can be performed either through mechanical means (mowing/pulling) or with herbicide. Consultation with a local Weed Inspector is highly recommended prior to the use of herbicide. Herbicides should be utilized sparingly and as a last resort. All herbicide applications should be in accordance with the manufacturer’s recommendations.

*Frequency* – Routine – As needed based upon inspections.

### GB-GS-3.5.5 Mosquito Treatment

GB-GS facilities are intended to drain, and should not have areas of standing water which creates mosquito habitat. Causes of the standing water or boggy conditions should be investigated and remediated as necessary to eliminate the standing water. Only EPA approved chemicals should be applied in accordance with the recommendations of the manufacturer. See Section GB-GS-2.3.1d.

*Frequency* –As needed based upon inspections.

### GB-GS-3.5.6 Level Spreader (Grass Buffer only)

Evidence of uneven flow and localized erosion downstream of the level spreader indicates the flow is not evenly distributed along the length of the spreader. Areas of erosion should be repaired, filled and revegetated. Causes for the erosion should be investigated and repaired.

*Frequency* – As needed based upon inspections.

### GB-GS-3.5.7 Rodent Damage

Small holes, piles of dirt, and raised burrows are evidence of rodent damage. Damaged areas should be repaired and revegetated. Consultation with an animal control specialist or the Division of Wildlife may be required for persistent problems.

*Frequency* – As needed based on inspections.

## **GB-GS-3.6 Minor Maintenance Activities**

#### This work consists of a variety of isolated or small-scale maintenance/operational problems. Most of this work can be completed by a small crew, hand tools, and small equipment. These items require approval by the City of Aurora. Completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance activity.

**Table GB-GS-3**

**Summary of Minor Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Indication Action is Needed:** | **Maintenance Action** |
|  |  |  |  |
| **Sediment Removal** | As needed. | Sediment build-up. | Remove and properly dispose of sediment. |
| **Erosion Repair** | As needed, based upon inspection. | Rills and gullies forming on slopes and other areas. | Repair eroded areas and  revegetate; address cause. |
| **Vegetation Removal** | As needed, based upon inspection | Trees, willows, shrubs impeding flow. | Remove vegetation; restore correct grade and surface. |
| **Revegetation** | As needed, based upon inspection. | Areas without grass. | Replace grass by sodding or seeding. |
| **Irrigation (Automatic)** | As needed, based upon inspection. | Evidence of broken or missing parts. | Replace parts and test system. |
| **Level Spreader (Grass Buffer Only)** | As needed, based upon inspection. | Evidence of uneven flow; erosion; or rills/gullies. | Repair sections of level spreader and address cause. |
| **Fertilization or Soil Amendment** | As needed, minimize fertilization. | Grass with pale color; areas with poor grass growth not due to irrigation problems. | Consult with turf specialist; Test soil. |
| **Vehicle Tracks (Along Roadways)** | As needed, based upon inspection. | Depressions from vehicle tracks; vegetation damage. | Repair and fill depressions; sod or seed damaged areas. |

### GB-GS-3.6.1 Sediment Removal

Sediment removal is necessary to ensure proper function of the grass swale or buffer. Care should be taken when removing sediment to prevent damage to the turf grass and surrounding areas. Excessive amounts of sediment are an indication of upstream erosion or lack of adequate BMPs during construction activities. Causes for contributions of excess sediment should be investigated and addressed.

*Frequency* – As needed based upon inspections.

### GB-GS-3.6.2 Erosion Repair

The repair of eroded areas is necessary to ensure the proper functioning of the GB-GS, to minimize sediment transport, and to reduce potential impacts to other features. Erosion can vary in magnitude from minor repairs to vegetation and embankments, to rills and gullies in the embankments and inflow points. The repair of eroded areas may require the use of excavators, riprap, new poured-in-place concrete, and sod. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system, if present, does not occur. Major erosion in a GS-GB is generally the result of excessive velocities caused by steep slopes. It may be necessary to make design improvements to the swale or buffer when erosion becomes a major maintenance item.

*Frequency* – As necessary, based upon inspections.

### GB-GS-3.6.3 Vegetation Removal

Weeds, Shrubs, Willows and other unwanted vegetation that develops in the grass swale or buffer area may impede the flow and cause standing water or back flow problems. It is necessary to remove unwanted vegetation as soon as it appears. Remove the unwanted vegetation, and restore the correct grade. Revegetate with seed or sod. Supplement irrigation as needed until new vegetation is sufficiently established.

*Frequency* – As necessary, based upon inspections.

### GB-GS -3.6.4 Revegetation

Bare areas should be repaired as soon as possible. Repair bare areas with appropriate grass seed or sod. Supplement irrigation as needed until new vegetation is sufficiently established. Causes of the problem, such as inadequate water supply or diseased grasses, should be investigated and resolved.

*Frequency* – As necessary, based upon inspections.

### GB-GS-3.6.5 Irrigation (Automatic)

Irrigation systems require routine maintenance in accordance with the manufacturer’s recommendations (valves, timer, etc.), and maintenance of the pipe and heads to ensure even coverage is being applied, and there are no missing or broken parts. Timing systems should be checked to verify the correct amount of water is being applied to the grassed areas for the seasonal conditions.

*Frequency* – As necessary, based upon inspections.

### GB-GS-3.6.6 Level Spreader

Level Spreaders that are no longer level, or have developed damaged areas of cracking or spalling, allow flows to concentrate in these depressed areas instead of being distributed over the length of the structure. Also, buildup of grasses along the edge of the spreader may create an uneven flow distribution. Rills, gullies and other erosion that develop downstream of level spreaders should be repaired and reseeded or sodded. Causes of the erosion should be investigated and addressed.

*Frequency* – As necessary, based upon inspections.

### GB-GS-3.6.7 Fertilization/Soil Amendment

Grass Buffers and Swales rely on healthy, dense turf in order to function properly. Grasses that appear to be diseased, dying or unhealthy may require amendments. Fertilizers should be applied in the minimum amounts recommended by the manufacturer. Check for insect infestation also.

*Frequency* – As necessary, based upon inspections.

### GB-GS-3.6.8 Vehicle Tracks

GB-GSs adjacent to roadway sections or drive aisles in parking lots may be damaged by vehicle tracks. Rutted areas should be filled in and revegetated as soon as possible. Frequent problems associated with vehicle traffic (such as around corners) may require a barrier or sign to avoid vehicular traffic within the grassed areas.

*Frequency –* As necessary, based upon inspections.

## **GB-GB-3.7 Major Maintenance Activities**

This work consists of larger maintenance/operational problems and failures within the stormwater management facilities. All of this work requires consultation with the City of Aurora Water Staff to ensure the proper maintenance is performed. This work requires the City of Aurora Water and Engineering Staff review the original design and construction drawings to assess the situation before approval of the proposed maintenance. This work may also require more specialized maintenance equipment, design/details, submittal of plans to the City of Aurora for review and approval, surveying, or assistance through private contractors and consultants.

**Table GB-GS-4**

**Summary of Major Maintenance Activities**

| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
| --- | --- | --- | --- |
|  |  |  |  |
| **Major Sediment/Pollutant Removal** | As needed – based upon scheduled inspections. | Large quantities of sediment. | Remove and dispose of sediment. Repair vegetation as needed. |
| **Major Erosion Repair** | As needed – based upon scheduled inspections. | Severe erosion including gullies, excessive soil displacement, areas of settlement, holes | Repair erosion – find cause of problem and address to avoid future erosion. |
| **Structural Repair** | As needed – based upon scheduled inspections. | Deterioration and/or damage to structural components – level spreader, grade control structures, irrigation components, and ponding water. | Structural repair to restore the structure to its original design. |
| **GB-GS Rebuild** | As needed – due to complete failure of BMP. | Removal of filter media and underdrain system. | Contact City of Aurora Water Staff |

### GB-GS-3.7.1 Major Sediment/Pollutant Removal

Major sediment removal consists of removal of large quantities of pollutants/sediment /landscaping material. Stormwater sediments removed from GB-GSs do not meet the regulatory definition of “hazardous waste”. However, these sediments can be contaminated with a wide array of organic and inorganic pollutants and handling must be done with care to insure proper removal and disposal. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a licensed landfill for proper disposal. Should a spill occur during transportation, prompt and thorough cleanup and disposal is imperative. Vegetated areas need special care to ensure design volumes and grades are preserved or may need to be replaced due to the removal activities.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

GB-GS-3.7.2 Major Erosion Repair

Major erosion repair consists of filling and revegetating areas of severe erosion. Determining the cause of the erosion as well as correcting the condition that caused the erosion should also be part of the erosion repair. Care should be given to ensure design grades and volumes are preserved.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### GB-GS-3.7.3 Structural Repair

A GB-GS generally includes level spreader and grade control structure that can deteriorate or be damaged during the service life of the facility. These structures are constructed of steel and concrete that can degrade or be damaged and may need to be repaired or re-constructed from time to time. Major repairs to structures may require input from a structural engineer and specialized contractors. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to all structural repairs.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### GB-GS-3.7.4 GB-GS Rebuild

In very rare cases, a GB-GS may need to be rebuilt. Generally, the need for a complete rebuild is a result of improper construction, improper maintenance resulting in structural damage to the underdrain system, if present, or extensive contamination of the GB-GS. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to any rebuild project.

*Frequency* – Non-routine – As needed based upon inspections.

Reference:

**This plan is adapted from Southeast Metro Stormwater Authority,** *Operation and Maintenance (O & M) MANUAL,* **and the Douglas County, Colorado,** *Standard Operating Procedure for Extended Detention Basin (EDB) Inspection and Maintenance,* July 2005

**Appendix C-3**

**Bioretention Cell**

**aka**

**Porous Landscape Detention**

Standard Operation Procedures

for

Inspection and Maintenance  
  
  
Bioretention Cell (BRCs)

aka

Porous Landscape Detention

(PLDs)



September 2010

**Table of Contents**

[**BRC/PLD-1 Background** 3](#_Toc120411671)

[**BRC/PLD-2 Inspecting Bioretention Cell (BRC) aka Porous Landscape Detention (PLD)** 3](#_Toc120411672)

[BRC/PLD-2.1 Access and Easements 3](#_Toc120411673)

[BRC/PLD-2.2 Stormwater Management Facilities Locations 3](#_Toc120411674)

[BRC/PLD-2.3 Bioretention Cell aka Porous Landscape Detention (PLD) Features 3](#_Toc120411675)

[BRC/PLD-2.3.1 Inflow Points 4](#_Toc120411676)

[BRC/PLD-2.3.2 Landscaping 5](#_Toc120411677)

[BRC/PLD-2.3.3 Filter Media 5](#_Toc120411678)

[BRC/PLD-2.3.4 Underdrain System 7](#_Toc120411679)

[BRC/PLD-2.3.5 Overflow Outlet Works 7](#_Toc120411680)

[BRC/PLD-2.3.6 Embankments 8](#_Toc120411681)

[BRC/PLD-2.3.7 Miscellaneous 8](#_Toc120411682)

[BRC/PLD-2.4 Inspection Forms 8](#_Toc120411683)

**BRC/PLD-3 Maintaining Bioretention Cells (BRCs) aka Porous Landscape Detentions (PLD)** 9

[BRC/PLD-3.1 Maintenance Personnel 9](#_Toc120411684)

[BRC/PLD-3.2 Equipment 9](#_Toc120411685)

[BRC/PLD-3.3 BRC/PLD Maintenance Forms 10](#_Toc120411686)

[BRC/PLD-3.4 BRC/PLD Maintenance Categories and Activities 10](#_Toc120411688)

[BRC/PLD-3.5 Routine Maintenance Activities 10](#_Toc120411689)

[BRC/PLD-3.5.1 Mowing 11](#_Toc120411690)

[BRC/PLD-3.5.2 Trash/Debris Removal 11](#_Toc120411691)

[BRC/PLD-3.5.3 Overflow Outlet Works Cleaning 11](#_Toc120411692)

[BRC/PLD-3.5.4 Weed Control 12](#_Toc120411693)

[BRC/PLD-3.6 Minor Maintenance Activities 12](#_Toc120411694)

[BRC/PLD-3.6.1 Sediment/Pollutant Removal 12](#_Toc120411695)

[BRC/PLD-3.6.2 Erosion Repair 15](#_Toc120411696)

[BRC/PLD-3.6.3 Jet-Vac/Clearing Drains 15](#_Toc120411697)

[BRC/PLD-3.7 Major Maintenance Activities 15](#_Toc120411698)

[BRC/PLD-3.7.1 Major Sediment/Pollutant Removal 16](#_Toc120411699)

[BRC/PLD-3.7.2 Major Erosion Repair 16](#_Toc120411700)

[BRC/PLD-3.7.3 Structural Repair 17](#_Toc120411701)

[BRC/PLD-3.7.4 BRC/PLD Rebuild 17](#_Toc120411702)

# **BRC/PLD-1 Background**

Bioretention Cell (BRC) aka Porous Landscape Detention (PLD) is a common type of Stormwater Management Facility utilized within the Front Range of Colorado. BRCs/PLDs consist of a low-lying vegetated area underlain by a sand bed with an underdrain pipe. A shallow surcharge zone exists above the BRC/PLD for temporary storage of the Water Quality Capture Volume (WQCV). During a storm, accumulated runoff ponds in the vegetated zone and gradually infiltrates into the underlying sand bed, filling the void spaces of the sand. The underdrain gradually dewaters the sand bed and discharges the runoff to a nearby channel, swale, or storm sewer. The BRC/PLD provides for filtering, adsorption, and biological uptake of constituents in stormwater[[1]](#footnote-1). The popularity of BRCs/PLDs has increased because they allow the WQCV to be provided on a site that has little open area available for stormwater management.

# **BRC/PLD-2 Inspecting Bioretention Cell (CELL) aka Porous Landscape Detention (PLD)**

## **BRC/PLD-2.1 Access and Easements**

Inspection or maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the access points and maintenance easements of the BRCs/PLDs within this development.

## **BRC/PLD-2.2 Stormwater Management Facilities Locations**

Inspection or maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the BRCs/PLDs within this development.

## **BRC/PLD-2.3 Bioretention Cell (BRC) aka Porous Landscape Detention (PLD) Features**

BRCs/PLDs have a number of features designed to serve a particular function. Many times the proper function of one feature depends on another. It is important for maintenance personnel to understand the function of each of these features to prevent damage to any feature during maintenance operations. Below is a list and description of the most common features within a BRC/PLD and the corresponding maintenance inspection items anticipated:

**Table BRC/PLD-1**

**Typical Inspection and Maintenance Requirements Matrix**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | **Sediment Removal** | **Mowing**  **Weed control** | **Trash/ Debris Removal** | **Erosion** | **Overgrown Vegetation Removal** | **Removal/ Replacement** | **Structure Repair** |
| Inflow Points | X |  | X |  |  |  | X |
| **Landscaping** | X | X | X | X | X |  |  |
| **Filter Media** | X | X | X | X | X | X |  |
| **Underdrain System** |  |  |  |  |  | X |  |
| **Overflow Outlet Works** | X |  | X |  |  |  | X |
| **Embankment** |  | X | X | X | X |  |  |

### BRC/PLD-2.3.1 Inflow Points

Inflow points or outfalls into BRCs/PLDs are the point of stormwater discharge into the facility. An inflow point is commonly a curb cut with a concrete or riprap rundown. In limited cases, a storm sewer pipe outfall with a flared end section may be the inflow point into the BRC/PLD.

An energy dissipater (riprap or concrete wall) is typically immediately downstream of the discharge point into the BRC/PLD to protect the BRC/PLD from erosion. In some cases, the storm sewer outfall can have a toe-wall or cut-off wall immediately below the structure to prevent undercutting of the outfall from erosion.

The typical maintenance items required at inflow points are as follows:

*a. Riprap Displaced* – Many times, because of the repeated impact/force of water, the riprap can shift and settle. If any portion of the riprap rundown or apron appears to have settled, soil is present between the riprap, or the riprap has shifted, maintenance may be required to ensure future erosion is prevented.

*b. Erosion Present/Outfall Undercut* – In some situations, the energy dissipater may not have been sized, constructed, or maintained appropriately and erosion has occurred. Any erosion within the vicinity of the inflow point will require maintenance to prevent damage to the structure(s) and sediment transport within the facility. It is imperative material utilized to correct erosion problems within the filter media meets the requirements for filter media as shown on the approved construction drawings.

*c. Sediment Accumulation* – Because of the turbulence in the water created by the energy dissipater, sediment often deposits immediately downstream of the inflow point. To prevent a loss in performance of the upstream infrastructure, sediment that accumulates in this area must be removed on a timely basis.

*d. Structural Damage* – Structural damage can occur at anytime during the life of the facility. Typically, for an inflow, the structural damage occurs to the concrete or riprap rundown or pipe flared end section (concrete, HDPE, or steel). Structural damage can lead to additional operating problems with the facility, including loss of hydraulic performance.

### BRC/PLD-2.3.2 Landscaping

The landscaped area consists of specific plant materials and associated landscaping mulch in the bottom of the BRC/PLD. These plantings provide several functions for the BRC/PLD. Planting not only provides an aesthetic value for the BRC/PLD, but in many cases assists with biological uptake or removal of pollutants.

The plants are carefully selected for use in the BRCs/PLDs. Plants utilized in BRCs/PLDs must be able to grow in dry sandy soils but also be able to withstand frequent inundation by stormwater runoff. These plants also must be able to withstand a variety of pollutants commonly found in stormwater runoff. In addition, plants utilized in BRCs/PLDs cannot have a deep extensive root system that may cause maintenance difficulty or damage to the facility.

*The typical maintenance activities required within the landscape areas are as follows:*

*a. Woody Growth/Weeds Present* – Undesirable vegetation can grow in and around the landscaped area in the BRC/PLD that can significantly affect the performance of the facility. This type of vegetation includes dense areas of shrubs (willows), grasses and noxious weeds. If undesired vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate, resulting in blockage of the filter media. Also, shrub, grass and weed roots can cause damage to the filter media and underdrain system. Routine management is essential to prevent more extensive and costly future maintenance.

*b. General Landscape Care* – The landscape elements of the BRC/PLD are the same as any other landscape area and need to be provided with regular care. Landscape mulch will need to be removed and replaced to ensure the aesthetics of the BRC/PLD.

### BRC/PLD-2.3.3 Filter Media

The filter media is the main pollutant removal component of the BRC/PLD. The filter media generally consists of eighteen (18) inches of a mixture of washed sand and peat. The filter media removes pollutants through several different processes, including sedimentation, filtration, absorption, infiltration and microbial uptake.

Sedimentation is accomplished by the slow release of stormwater runoff through the filter media. This slow release allows sediment particles to be deposited on the top layer of the filter media where they are easily removed through routine maintenance. Other pollutants are also removed through this process because many pollutants utilize sediment as a transport mechanism.

Filtration is the main pollutant removal mechanism of BRCs/PLDs. When the stormwater runoff migrates down through the filter media, many of the particulate pollutants are physically strained out as they pass through the filter bed of sand and are trapped on the surface or among the pores of the filter media.[[2]](#footnote-2)

Absorption results from the peat utilized in the filter media. Organic materials have a natural ability to attach to soluble nutrients, metals and organic pollutants. This attachment then prevents these pollutants from leaving the BRC/PLD.

BRCs/PLDs not lined with an impervious liner allow for infiltration into the native soils. This process also allows for additional pollutant removal.

Microbes that naturally occur in the filter media can assist with pollutant removal by breaking down organic pollutants.

The typical maintenance activities required within the filter media areas are as follows:

*a. Infiltration Rate Check* – The infiltration rate of the BRC/PLD needs to be checked in order to ensure proper functioning of the BRC/PLD. Generally, a BRC/PLD should drain completely within twelve (12) hours of a storm event. If drain times exceed the twelve (12) hour drain time then maintenance of the filter media shall be required.

*b. Sediment Removal* – Although BRCs/PLDs should not be utilized in areas where large concentrations of sediment may enter the BRC/PLD, it is inevitable that some sediment will enter the BRC/PLD.

*c. Filter Replacement* - The top layers of the filter media are the most susceptible to pollutant loading and therefore may need to be removed and disposed of properly on a semi-regular basis when infiltration rates slow.

**BRC/PLD-2.3.4 Underdrain System**

The underdrain system consists of a layer of geotextile fabric, gravel storage area and perforated PVC pipes. The geotextile fabric is utilized to prevent the filter media from entering the underdrain system. The gravel storage area allows for storage of treated stormwater runoff prior to the discharge of the runoff through the perforated PVC pipe.

*The typical maintenance activities for the underdrain system are as follows:*

With proper maintenance of the landscape areas and filter media, there should be a minimum amount of maintenance required on the underdrain system. Generally the only maintenance performed on the underdrain system is jet-vac cleaning.

### BRC/PLD-2.3.5 Overflow Outlet Works

Generally, the initial runoff (“first flush”) or WQCV during the storm event contains the majority of the pollutants. BRCs/PLDs are designed to treat only the WQCV and any amount over the WQCV is allowed to go to a detention facility without water quality treatment. The overflow outlet works allows runoff amounts over the WQCV to exit the BRC/PLD to the detention facility. The outlet works is typically constructed of a reinforced concrete box in the embankment of the BRC/PLD. The concrete structure typically has a steel grate to trap litter and other debris from entering the storm sewer system. Proper inspection and maintenance of the outlet works is essential in ensuring the long-term operation of the BRC/PLD.

The most typical maintenance items found with overflow outlet works are as follows:

*a. Structural Damage* - The overflow outlet structure is primarily constructed of concrete, which can crack, spall, and settle. The steel grate on the overflow outlet structure is also susceptible to damage.

*b. Woody Growth/Weeds Present* – The presence of plant material not part of the original landscaping, such as wetland plants or other woody growth, can clog the overflow outlet works during a larger storm event, causing flooding damage to adjacent areas. This plant material may indicate a clogging of the filter media and may require additional investigation.

*c. Trash/Debris* – Trash and debris can accumulate in the upper area after large events, or from illegal dumping. Over time, this material can clog the BRC/PLD outlet works.

**BRC/PLD-2.3.6 Embankments**

Some BRCs/PLDs utilize irrigated turf grass embankment to store the WQCV.

The typical maintenance activities required with the embankments areas are as follows:

*a. Vegetation Sparse* – The embankments are one of the most visible parts of the BRC/PLD, and therefore aesthetics is important. Adequate and properly maintained vegetation can greatly increase the overall appearance of the BRC/PLD. Vegetation can reduce the potential for erosion and subsequent sediment transport to the filter media, thereby reducing the need for more costly maintenance.

*b. Erosion* – Inadequate vegetative cover may result in erosion of the embankments. Erosion that occurs on the embankments can cause clogging of the filter media. Repair to these erosion areas including revegetation is required.

### BRC/PLD-2.3.7 Miscellaneous

There are a variety of inspection/maintenance issues that may not be attributed to a single feature within the BRC/PLD. This category on the inspection form is for maintenance items that are commonly found in the BRC/PLD, but may not be attributed to an individual feature.

*a. Encroachment in Easement Area* – Private lots/property can sometimes be located very close to the BRCs/PLDs, even though the City of Aurora requires BRCs/PLDs be located, at a minimum, within drainage easements. Property owners may not place landscaping, trash, fencing, or other items within the easement area that may adversely affect maintenance or the operation of the facility.

*b. Graffiti/Vandalism* – Vandals can cause damage to the BRC/PLD infrastructure. If criminal mischief is evident, the inspector should forward this information to the Aurora Police Department.

*c. Public Hazards* – Public hazards include items such as containers of unknown/suspicious substances, and exposed metal/jagged concrete on structures. **If any unknown/suspicious hazard is found within the facility area that poses an immediate threat to public safety, call 911 immediately.**

*d. Other* – Any miscellaneous inspection/maintenance items not contained on the form should be entered here.

## **BRC/PLD-2.4 Inspection Forms**

BRC/PLD Inspection forms are located in Appendix D. Inspection forms shall be completed by the person(s) conducting the inspection activities. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. These inspection forms shall be kept indefinitely and made available to the City of Aurora upon request.

# **BRC/PLD-3 Maintaining Bioretention Cell aka Porous Landscape Detentions (PLD)**

## **BRC/PLD-3.1 Maintenance Personnel**

Maintenance personnel must be experienced to properly maintain BRCs/PLDs. Inadequately trained personnel can cause additional problems resulting in additional maintenance costs.

## **BRC/PLD-3.2** **Equipment**

It is imperative the appropriate equipment and tools are taken to the field with the operations crew. The types of equipment/tools will vary depending on the task at hand. Below is a basic list of tools, equipment, and material(s) that may be necessary to perform maintenance on a BRC/PLD:

1. Mowing Tractors
2. Trimmers (extra string)
3. Shovels
4. Rakes
5. All Surface Vehicle (ASVs)
6. Skid Steer
7. Back Hoe
8. Track Hoe/Long Reach Excavator
9. Dump Truck
10. Jet-Vac Machine
11. Engineers Level (laser)
12. Riprap (Minimum - Type M)
13. Geotextile Fabric
14. Erosion Control Blanket(s)
15. Sod
16. Illicit Discharge Cleanup Kits
17. Trash Bags
18. Tools (wrenches, screw drivers, hammers, etc)
19. Confined Space Entry Equipment
20. Approved Stormwater Facility Inspection and Maintenance Plan
21. ASTM C-33 Sand
22. Peat
23. Wood Landscaping Mulch

Some of the items identified above may not be needed for every maintenance operation. However, this equipment should be available to the maintenance operations crews should the need arise.

## **BRC/PLD-3.3 BRC/PLD Maintenance Forms**

The BRC/PLD Maintenance Form provides a record of each maintenance operation performed by maintenance contractors. The BRC/PLD Maintenance Form shall be filled out in the field after the completion of the maintenance operation. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. The BRC/PLD Maintenance form is located in Appendix E.

## **BRC/PLD-3.4 BRC/PLD Maintenance Categories and Activities**

A typical BRC/PLD Maintenance Program will consist of three broad categories of work: Routine, Minor and Major. Within each category of work, a variety of maintenance activities can be performed on a BRC/PLD. A maintenance activity can be specific to each feature within the BRC/PLD, or general to the overall facility. This section of the SOP explains each of the categories and briefly describes the typical maintenance activities for a BRC/PLD.

A variety of maintenance activities is typical of BRCs/PLDs. The maintenance activities range in magnitude from routine trash pickup to the reconstruction of the BRC/PLD filter media or underdrain system. Below is a description of each maintenance activity, the objectives, and frequency of actions:

# **BRC/PLD-3.5 Routine Maintenance Activities**

The majority of this work consists of scheduled mowings, trash and debris pickups and landscape care for the BRC/PLD during the growing season. It also includes activities such as weed control. These activities normally will be performed numerous times during the year. These items do notrequire any prior approval by the City of Aurora, however, completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance activity in accordance with the Inspection and Maintenance Plan.

The Routine Maintenance Activities are summarized below, and further described in the following sections.

**Table BRC/PLD-2**

**Summary of Routine Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Mowing** | Twice annually | Excessive grass height/aesthetics | 2”-4” grass height |
| **Trash/Debris Removal** | Twice annually | Trash & debris in BRC/PLD | Remove and dispose of trash/debris |
| **Overflow Outlet Works Cleaning** | As needed - after significant rain events – twice annually minimum | Clogged outlet structure; ponding water above outlet elevation | Remove and dispose of debris/trash/sediment to allow outlet to function properly |
| **Weed Control** | As needed, based upon inspection | Noxious weeds; Unwanted vegetation | Treat w/herbicide or hand pull; consult a local Weed Inspector |

### BRC/PLD-3.5.1 Mowing

Routine mowing of the turf grass embankments is necessary to improve the overall appearance of the BRC/PLD. Turf grass should be mowed to a height of two (2) to four (4) inches and shall be bagged to prevent potential contamination of the filter media.

*Frequency* – Routine - Minimum of twice annually or depending on aesthetics.

### BRC/PLD-3.5.2 Trash/Debris Removal

Trash and debris must be removed from the entire BRC/PLD area to minimize outlet clogging and to improve aesthetics. This activity must be performed prior to mowing operations.

*Frequency –* Routine – Prior to mowing operations and minimum of twice annually.

### BRC/PLD-3.5.3 Overflow Outlet Works Cleaning

Debris and other materials can clog the overflow outlet work’s grate. This activity must be performed anytime other maintenance activities are conducted to ensure proper operation.

*Frequency* - Routine – After significant rainfall event or concurrently with other maintenance activities.

BRC/PLD-3.5.4 Weed Control

Noxious weeds and other unwanted vegetation must be treated as needed throughout the BRC/PLD. This activity can be performed either through mechanical means (mowing/pulling) or with herbicide. Consultation with a local Weed Inspector is highly recommended prior to the use of herbicide. Herbicides should be utilized sparingly and as a last resort. All herbicide applications should be in accordance with the manufacturer’s recommendations.

*Frequency –* Routine – As needed based on inspections.

# **BRC/PLD-3.6 Minor Maintenance Activities**

#### This work consists of a variety of isolated or small-scale maintenance/operational problems. Most of this work can be completed by a small crew, hand tools, and small equipment. These items require approval by the City of Aurora Water Staff. Completed inspection and maintenance forms shall be submitted to City of Aurora for each inspection and maintenance period. In the event the BRC/PLD needs to be dewatered, care should be given to ensure sediment, filter material and other pollutants are not discharged. All dewatering activities shall be coordinated with the City of Aurora Water Staff.

**Table BRC/PLD-3**

**Summary of Minor Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Sediment/Pollutant Removal** | As needed; Based on infiltration test | Sediment build-up; decrease in infiltration rate | Remove and dispose of sediment |
| **Erosion Repair** | As needed, based upon inspection | Rills/gullies forming on embankments | Repair eroded areas &  revegetate; address cause |
| **Jet Vac/Cleaning underdrain system** | As needed, based upon inspection | Sediment build-up /non draining system | Clean drains; Jet-Vac if needed |

### 

### BRC/PLD-3.6.1 Sediment/Pollutant Removal

Sediment/Pollutant removal is necessary to ensure proper function of the filter media. The infiltration rate of the BRC/PLD needs to be checked in order to ensure proper functioning of the BRC/PLD. Generally, a BRC/PLD should drain completely within twelve (12) hours of a storm event. If drain times exceed the twelve (12) hour drain time then maintenance of the filter media shall be required.

Generally, the top three (3) inches of filter media should be removed at each removal period. Additional amounts of filter media may need to be removed if deeper sections of the filter media are contaminated. New filter media will need to replace the removed filter media. It is critical only sand meeting the American Society for Testing and Materials (ASTM) C-33 standard be utilized in the replacement of the filter media (Note: The update to the UDFCD’s Volume III manual, to be released in late 2010, may have new filter media guidelines).

**ASTM C-33 Sand Standard**

|  |  |
| --- | --- |
| **US Standard Sieve Size (Number)** | **Total Percent Passing (%)** |
| 9.5 mm (3/8 inch) | 100 |
| 4.75 mm (No. 4) | 95-100 |
| 2.36 mm (No. 8) | 80-100 |
| 1.18 mm (No. 16) | 50-85 |
| 6000085mm (No | 25-60 |
| 3000060mm (No | 10-30 |
| 1505030mm (No. | 2-10 |

In addition, only Peat Moss meeting the following specifications shall be utilized with the filter media.

|  |  |
| --- | --- |
| **pH (Units)** | **7.6** |
| **Total Salts (MMHOS/CM, 1:5)** | **2.28** |
| **Organic Matter (%)** | **20.22** |
| **Moisture (%)** | **21.43** |
| **Dry Matter Basis:** | |
| **Nitrogen - Total (%)** | **0.780** |
| **Nitrogen - Organic (%)** | **0.773** |
| **Nitrogen - Ammonia (PPM)** | **46.8** |
| **Nitrogen - Nitrate (PPM)** | **31.3** |
| **Total Phosphorus (%) as P (%) as P2O5** | **0.103 0.237** |
| **Total Potassium (%) as K (%) as K2O** | **0.138 0.166** |
| **Carbon / Nitrogen Ratio** | **13.6** |

Other types of sand or soil material may lead to clogging of the BRC/PLD (Note: The update to the UDFCD’s Volume III manual, to be released in late 2010, may have new filter media guidelines). The minor sediment removal activities can typically be addressed with shovels, rakes, and smaller equipment. Major sediment removal activities will require larger and more specialized equipment. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur. The major sediment removal activities will also require surveying with an engineer’s level, and consultation with the City of Aurora Water and Engineering Staff to ensure design volumes/grades are achieved.

Stormwater sediments removed from BRCs/PLDs do not meet the regulatory definition of “hazardous waste”. However, these sediments can be contaminated with a wide array of organic and inorganic pollutants and handling must be done with care. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a licensed landfill for proper disposal. Should a spill occur during transportation, prompt and thorough cleanup and disposal is imperative.

*Frequency* – Non-routine – As necessary, based upon inspections and infiltration tests. Sediment removal in the forebay and trickle channel may be necessary as frequently as every one (1) to two (2) years.

### BRC/PLD-3.6.2 Erosion Repair

The repair of eroded areas is necessary to ensure the proper functioning of the BRC/PLD, to minimize sediment transport, and to reduce potential impacts to other features. Erosion can vary in magnitude from minor repairs to filter media and embankments, to rills and gullies in the embankments and inflow points. The repair of eroded areas may require the use of excavators, earthmoving equipment, riprap, concrete, and sod. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur. Major erosion repair to the pond embankments, spillways, and adjacent to structures will require consultation with the City of Aurora Water and Engineering Staff.

*Frequency* – Non-routine – As necessary, based upon inspections.

### BRC/PLD-3.6.3 Jet-Vac/Clearing Drains

A BRC/PLD contains an underdrain system that allows treated stormwater runoff to exit the facility. These underdrain systems can develop blockages resulting in a decrease of hydraulic capacity and creating standing water. Many times the blockage to this infrastructure can be difficult to access and/or clean. Specialized equipment (jet-vac machines) may be necessary to clear debris from these difficult areas.

*Frequency –* Non-routine – As necessary, based upon inspections.

# **BRC/PLD-3.7 Major Maintenance Activities**

This work consists of larger maintenance/operational problems and failures within the stormwater management facilities. All of this work requires consultation with the City of Aurora Water and Engineering to ensure the proper maintenance is performed. This work requires Staff review the original design and construction drawings to assess the situation before approval of the proposed maintenance. This work may also require more specialized maintenance equipment, design/details, submittal of plans to the City of Aurora for review and approval, surveying, or assistance through private contractors and consultants.

**Table BRC/PLD-4**

**Summary of Major Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Major Sediment/Pollutant Removal** | As needed – based upon scheduled inspections | Large quantities of sediment; reduced pond capacity | Remove and dispose of sediment. Repair vegetation as needed |
| **Major Erosion Repair** | As needed – based upon scheduled inspections | Severe erosion including gullies forming, excessive soil displacement, areas of settlement, holes | Repair erosion – find cause of problem and address to avoid future erosion |
| **Structural Repair** | As needed – based upon scheduled inspections | Deterioration and/or damage to structural components – broken concrete, damaged pipes & outlet works | Structural repair to restore the structure to its original design |
| **BRC/PLD Rebuild** | As needed – due to complete failure of BRC/PLD | Removal of filter media and underdrain system | Contact the City of Aurora Water and Engineering Staff |

### BRC/PLD-3.7.1 Major Sediment/Pollutant Removal

Major sediment removal consists of removal of large quantities of pollutants/sediment/filter media/landscaping material. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur. Some BRCs/PLDs also contain an impermeable liner that can be easily damage if care is not taken when removing the filter media. Stormwater sediments removed from BRCs/PLDs do not meet the regulatory definition of “hazardous waste”. However, these sediments can be contaminated with a wide array of organic and inorganic pollutants and handling must be done with care to ensure proper removal and disposal. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a licensed landfill for proper disposal. Should a spill occur during transportation, prompt and thorough cleanup and disposal is imperative. Vegetated areas need special care to ensure design volumes and grades are preserved or may need to be replaced due to the removal activities. Any condition repair affecting design grades or pond volumes requires consultation with the City of Aurora Water and Engineering Staff

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### BRC/PLD-3.7.2 Major Erosion Repair

Major erosion repair consists of filling and revegetating areas of severe erosion. Determining the cause of the erosion as well as correcting the condition that caused the erosion should also be part of the erosion repair. Care should be given to ensure design grades and volumes are preserved. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### BRC/PLD-3.7.3 Structural Repair

A BRC/PLD generally includes a concrete overflow outlet structure that can deteriorate or be damaged during the service life of the facility. These structures are constructed of steel and concrete that can degrade or be damaged and may need to be repaired or re-constructed from time to time. Major repairs to structures may require input from a structural engineer and specialized contractors. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to all structural repairs.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### BRC/PLD-3.7.4 BRC/PLD Rebuild

In very rare cases, a BRC/PLD may need to be rebuilt. Generally, the need for a complete rebuild is a result of improper construction, improper maintenance resulting in structural damage to the underdrain system, or extensive contamination of the BRC/PLD. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to any rebuild project. Recertification of the BRC/PLD in accordance with the City’s drainage criteria manual is required.

*Frequency* – Non-routine – As needed based upon inspections.

Reference:

**This plan is adapted from Southeast Metro Stormwater Authority,** *Operation and Maintenance (O & M) Manual,* **and the Douglas County, Colorado,** *Standard Operating Procedure for Extended Detention Basin (EDB) Inspection and Maintenance,* July 2005

**Appendix C-4**

**Sand Filter Basins**

Standard Operation Procedures

for

Inspection and Maintenance

Sand Filter Basins

(SFBs)



June 2016

**Table of Contents**

**SFB-1 Background 21**

**SFB-2 Inspecting Sand Filter Basins (SFBs) 21**

SFB-2.1 Access and Easements 21

SFB-2.2 Stormwater Management Facilities Locations 21

SFB-2.3 Sand Filter Extended Detention Basin (SFB) Features 21

SFB-2.3.1 Inflow Points/Splitter Box 22

SFB-2.3.2 Sedimentation Chamber 23

SBF-2.3.3 Filter Media 24

SFB-2.3.4 Underdrain System 25

SFB-2.3.5 Overflow Outlet Works 25

SFB-2.3.6 Embankments 26

SFB-2.3.7 Emergency Overflow 27

SFB-2.3.8 Miscellaneous 27

SFB-2.4 Inspection Forms 28

**SFB-3 Maintaining Sand Filter Basins (SFBs) 28**

SFB-3.1 Maintenance Personnel 28

SFB-3.2 Equipment 28

SFB-3.3 Safety 29

SFB-3.4 SFB Maintenance Forms 29

SFB-3.5 SFB Maintenance Categories and Activities 29

SFB-3.6 Routine Maintenance Activities 29

SFB-3.6.1 Mowing 30

SFB-3.6.2 Trash/Debris Removal 30

SFB-3.6.3 Splitter Box/Overflow Outlet Works Cleaning 30

SFB- 3.6.4 Woody Growth Control/Weed Removal 31

SFB-3.7 Minor Maintenance Activities 31

SFB-3.7.1 Sediment Removal/Pollutant Removal 31

SFB-3.7.2 Erosion Repair 33

SFB-3.7.3 Jet-Vac/Clearing Drains 33

SFB-3.8 Major Maintenance Activities 33

SFB-3.8.1 Major Sediment/Pollutant Removal 34

SFB-3.8.2 Major Erosion Repair 35

SFB-3.8.3 Structural Repair 35

SFB-3.8.4 SFB Rebuild 35

**SFB-1 Background**

Sand Filter Basins (SFBs) are a common type of Stormwater Management facility utilized within the Front Range of Colorado. A SFB consists of a sedimentation chamber, a flat surfaced area of sand (sometimes covered with grass or sod), a filtration chamber, and a flat sand filter bed with an underdrain system. A surcharge zone exists within the sedimentation and filtration chambers for temporary storage of the Water Quality Capture Volume (WQCV). During a storm, runoff enters the sedimentation chamber, where the majority of sediments are deposited. The runoff then enters the filtration chamber where it ponds above the sand bed and gradually infiltrates into the underlying sand filter, filling the void spaces of the sand. The underdrain gradually dewaters the sand bed and discharges the runoff to a nearby channel, swale, or storm sewer. SFBs provide for filtering and absorption of pollutants in the stormwater[[3]](#footnote-3). The popularity of SFBs has grown because they allow the WQCV to be provided on a site that has little open area available for stormwater management. However, there are limitations on their use due to potential clogging from large amounts of sediment.

# **SFB-2 Inspecting Sand Filter Basins (SFBs)**

## 

## **SFB-2.1 Access and Easements**

Inspection and maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the access points and maintenance easements of the SFBs within this development.

## **SFB-2.2 Stormwater Management Facilities Locations**

Inspection and maintenance personnel may utilize the stormwater facility map located in Appendix G containing the locations of the SFBs within this development.

## **SFB-2.3 Sand Filter Extended Detention Basin (SFB) Features**

SFBs have a number of features designed to serve a particular function. Many times the proper function of one feature depends on another. It is important for maintenance personnel to understand the function of each of these features to prevent damage to any feature during maintenance operations. Below is a basic list and description of the most common features within a SFB and the corresponding maintenance inspection items that may be anticipated:

**Table SFB-1**

**Typical Inspection & Maintenance Requirements Matrix**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | **Sediment Removal** | **Mowing**  **Weed control** | **Trash/ Debris Removal** | **Erosion** | **Overgrown Vegetation Removal** | **Removal/ Replacement** | **Structure Repair** |
| **Inflow Points/Splitter Box** | X |  | X |  |  |  | X |
| **Sedimentation Chamber** | X | X | X | X | X |  |  |
| **Filter Media** | X | X | X | X | X | X |  |
| **Underdrain System** |  |  |  |  |  | X |  |
| **Overflow Outlet Works** | X |  | X |  |  |  | X |
| **Embankment** |  | X | X | X | X |  |  |

### SFB-2.3.1 Inflow Points/Splitter Box

Inflow points or outfalls into SFBs are the point of stormwater discharge into the facility. An inflow point is commonly a curb cut with a concrete or riprap rundown or a storm sewer pipe outfall with a flared end section.

In some instances SFBs are designed to treat only the WQCV. The WQCV is a volume of water that runs off a site during an 80th percentile event. Any amount over the WQCV is allowed to go to a detention facility without water quality treatment. The splitter box is generally constructed of reinforced concrete. The splitter box typically has a lower wall height that will trap the required WQCV. Volumes over the WQCV are allowed to spill over the wall and enter a storm sewer system that conveys the runoff to a detention facility. Proper inspection and maintenance of the splitter box is essential in ensuring the long-term operation of the SFB.

An energy dissipater is typically immediately downstream of the splitter box, at the discharge point into the SFB, to protect the sedimentation and filtration chambers from erosion. In some cases, the splitter box outfall can have a toe-wall or cut-off wall immediately below the structure to prevent undercutting of the outfall from erosion.

Where there is detention included with the SFB an energy dissipater (riprap or hard armor protection) is typically immediately downstream of the discharge point into the SFB to protect from erosion. In some cases, the storm sewer outfall can have a toe-wall or cut-off wall immediately below the structure to prevent undercutting of the outfall from erosion.

*The typical maintenance activities required at inflow points are as follows:*

* 1. *Riprap Displaced* – Many times, because of the repeated impact/force of water, riprap can shift and settle. If any portion of the riprap apron appears to have settled, soil is present between the riprap, or the riprap has shifted, maintenance may be required to ensure future erosion is prevented.

1. *Sediment Accumulation* – Because of the turbulence in the water created by the energy dissipater, sediment often deposits immediately downstream of the inflow point. To prevent a loss in performance of the upstream infrastructure, sediment that accumulates in this area must be removed on a timely basis.
2. *Structural Damage* – Structural damage can occur at any time during the life of the facility. Typically for an inflow, the structural damage occurs to the pipe flared end section (concrete or steel). Structural damage can lead to additional operating problems with the facility, including loss of hydraulic performance.

### SFB-2.3.2 Sedimentation Chamber (Forebay)

The sedimentation chamber is located adjacent to the splitter box (inflow point) and generally consists of a flat irrigated turf grass area followed by a water trapping device allowing water to be briefly held in the sedimentation chamber before being released into the filtration chamber. This slowing of the runoff allows sediments/trash to be deposited in the sedimentation chamber (forebay) and not the filtration chamber where they can cause clogging of the filter media.

*The typical maintenance activities required within the sedimentation chamber are as follows:*

1. *Mowing/woody growth control/weeds present -* Routine mowing of the turf grass within the sediment chamber is necessary to improve the overall appearance and to ensure proper function of the SFB. Turf grass should be mowed to a height of two (2) to four (4) inches and shall be bagged to prevent potential contamination of the filter media. Before mowing any trash/debris should be removed and properly disposed. If undesirable vegetation is not routinely mowed/removed, the growth can cause debris/sediment to accumulate, resulting in blockage of the filter media. Also, shrub, grass and weed roots can cause damage to the filter media and underdrain system. Routine management is essential to prevent more extensive and costly future maintenance.

SBF-2.3.3 Filter Media

The filter media is the main pollutant removal component of the SFB. The filter media consists of eighteen (18) inches of washed sand. The filter media removes pollutants through several different processes, including sedimentation, filtration, infiltration and microbial uptake.

Sedimentation is accomplished by the slow release of stormwater runoff through the filter media. This slow release allows for sediment particles that were not deposited in the sedimentation chamber to be deposited on the top layer of the filter media where they are easily removed through routine maintenance. Other pollutants are also removed through this process because they are attached to sediment.

Filtration is the main pollutant removal mechanism of SFBs. When the stormwater runoff migrates down through the filter media, many of the particulate pollutants are physically strained out as they pass through the filter bed of sand and are trapped on the surface or among the pores of the filter media.

SFBs not lined with an impervious liner allow for infiltration into the native soils. This process also allows for additional pollutant removal.

Microbes that naturally occur in the filter media can assist with pollutant removal by breaking down organic pollutants.

The typical maintenance activities required within the filter media areas are as follows:

1. *Mowing/woody growth control/weeds present -* Noxious weeds and other unwanted vegetation must be treated as needed throughout the SFB. This activity can be performed either through mechanical means (mowing/pulling) or with herbicide. Consultation with a local Weed Inspector is highly recommended prior to the use of herbicide. Herbicides should be utilized sparingly and as a last resort. All herbicide applications should be in accordance with the manufacturer’s recommendations.
2. *Sediment/Pollutant Removal* – Although SFBs should not be utilized in areas where large concentrations of sediment and other pollutants will enter the SFB, it is inevitable some sediment and other pollutants will enter the SFB. Most sediment will be deposited in the sedimentation chamber (forebay), however finer suspended particles will migrate to the filter media. These sediments need to be removed to ensure proper infiltration rates of the stormwater runoff.
3. *Filter Replacement* - The top layers of the filter media are the most susceptible to pollutant loading and therefore may need to be removed and disposed of properly on a semi-regular basis when infiltration rates slow.
4. *Infiltration Rate Test* - An infiltration test may be necessary to ensure proper functioning of the filter media. The infiltration test can be conducted by filling the sand filter with water to the design elevation shown on the design drawings. The sand filter needs to drain completely within twenty-four (24) hours of the filling. If the drain time for the basin is longer than twenty-four (24) hours, the filter is in need of maintenance.

### SFB-2.3.4 Underdrain System

The underdrain system consists of a layer of geotextile fabric, gravel storage area and perforated PVC pipes. The geotextile fabric is utilized to prevent the filter media from entering the underdrain system. The gravel storage area allows for storage of treated stormwater runoff prior to the discharge of the runoff through the perforated PVC pipe.

*The typical maintenance activities required for the underdrain system are as follows:*

With proper maintenance of the filter media and sediment chamber, there should be a minimum amount of maintenance required on the underdrain system. Generally, the only maintenance performed on the underdrain system is jet-vac cleaning.

### SFB-2.3.5 Outlet Works

Where SFBs do not have a detention component the outlet works may take the place of the splitter box. If this is the case the outlet works includes an overflow. The overflow outlet works allows runoff amounts exceeding the WQCV to exit the SFB to the detention facility.

When the SFB does have a detention component the outlet works is typically constructed of reinforced concrete into the embankment of the SFB. The concrete structure typically has steel orifice plates anchored/embedded into it to control stormwater release rates. The larger openings (flood control) on the outlet structure typically have trash racks over them to prevent clogging. Proper inspection and maintenance of the outlet works is essential in ensuring the long-term operation of the SFB.

*The typical maintenance activities required for the overflow outlet works are as follows:*

1. *Trash Rack/Well Screen Clogged in an SFB with Detention Component* - Floatable material entering the SFB will most likely make its way to the outlet structure. This material is trapped against the trash racks and well screens on the outlet structure (which is why they are there). This material must be removed on a routine basis to ensure the outlet structure drains in the specified design period.
2. *Structural Damage* - The overflow outlet structure is primarily constructed of concrete, which can crack, spall, and settle. The steel grate on the overflow outlet structure (is so equipped), steel trash racks and well screens (if so equipped) are also susceptible to damage.
3. *Orifice Plate Missing/Not Secure in an SFB with Detention Component* - Many times residents, property owners, or maintenance personnel will remove or loosen orifice plates if they believe the pond is not draining properly. Any modification to the orifice plate(s) will significantly affect the designed discharge rates for flood control. Modification of the orifice plates is not allowed without approval from the City of Aurora Public Works Department, Engineering Control Division.
4. *Mowing/woody growth control/weeds present* – SFBs without the detention component the presence of plant material not part of the original landscaping, such as wetland plants or other woody growth, can clog the overflow outlet works during a larger storm event, causing flooding damage to adjacent areas. This plant material may indicate a clogging of the filter media and may require additional investigation.

In SFBs with the detention component woody vegetation not routinely mowed/removed may cause additional sediment/debris to accumulate around the outlet works. Any tree roots present can cause damage to the structural components of the outlet works. Routine management is essential for trees (removing a small tree/sapling is much cheaper and “quieter” than a mature tree).

### SFB-2.3.6 Embankments

Some SFBs utilize irrigated turf grass embankments to store the required volume.

*The typical maintenance activities required for the embankments areas are as follows:*

*a. Vegetation Sparse* – The embankments are one of the most visible parts of the SFB and, therefore, aesthetics is important. Adequate and properly maintained vegetation can greatly increase the overall appearance of the SFB. Also, vegetation can reduce the potential for erosion and subsequent sediment transport to the filter media, thereby reducing the need for more costly maintenance.

*b. Erosion* – Inadequate vegetative cover may result in erosion of the embankments. Erosion that occurs on the embankments can cause clogging of the filter media.

*c. Trash/Debris* – Trash and debris can accumulate in the upper area after large events, or from illegal dumping. Over time, this material can clog the SFB filter media and outlet works.

*d. Mowing/woody growth control/weeds present* – The presence of plant material not part of the original landscaping, such as wetland plants or other woody growth, can result in difficulty in performing maintenance activities. These trees and shrubs may also damage the underdrain system of the SFB. This plant material may indicate a clogging of the filter media and may require additional investigation.

### SFB-2.3.7 Emergency Overflow

An emergency spillway is typical of all SFBs and designed to serve as the overflow in the event the volume of the pond is exceeded. The emergency spillway is typically armored with riprap (or other hard armor), and is sometimes buried with soil or may be a concrete wall or other structure. The emergency spillway is typically a weir (notch) in the basin embankment. Proper function of the emergency spillway is essential to ensure flooding does not affect adjacent properties.

*The typical maintenance activities required for the emergency overflow areas are as follows:*

1. *Riprap Displaced* – As mentioned before, the emergency spillway is typically armored with riprap to provide erosion protection. Over the life of an SFB, the riprap may shift or become dislodged due to flow.
2. *Erosion Present* – Although the spillway is typically armored, stormwater flowing through the spillway can cause erosion damage. Erosion must be repaired to ensure the integrity of the basin embankment, and proper function of the spillway.
3. *Mowing/weed/woody growth control* – Management of woody vegetation is essential in the proper long-term function of the spillway. Larger trees or dense shrubs can capture larger debris entering the SFB and reduce the capacity of the spillway. These trees and shrubs may also damage the underdrain system of the SFB.
4. *Obstruction/Debris* – The spillway must be cleared of any obstruction (man-made or natural) to ensure the proper design capacity.

### SFB-2.3.8 Miscellaneous

There are a variety of inspection/maintenance issues that may not be attributed to a single feature within the SFB. This category on the inspection form is for maintenance items commonly found in the SFB, but may not be attributed to an individual feature.

1. *Encroachment in Easement Area* – Private lots/property can sometimes be located very close to the SFBs, even though they are required to be located in tracts with drainage easements. Property owners may not place landscaping, trash, fencing, or other items within the easement area that may adversely affect maintenance or the operation of the facility.
2. *Graffiti/Vandalism* – Vandals can cause damage to the SFB infrastructure. If criminal mischief is evident, the inspector should forward this information to the Aurora Police Department.
3. *Public Hazards* – Public hazards include items such as vertical drops of greater than four (4) feet, containers of unknown/suspicious substances, and exposed metal/jagged concrete on structures. **If any unknown/suspicious hazard is found within the facility area that poses an immediate threat to public safety, call 911 immediately.**
4. *Other –* Any miscellaneous inspection/maintenance items not contained on the form should be entered here.

## **SFB-2.4 Inspection Forms**

SFB Inspection forms are located in Appendix D. Inspection forms shall be completed by the person(s) conducting the inspection activities. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. These inspection forms shall be kept indefinitely and made available to the City of Aurora upon request.

# 

# **SFB-3 Maintaining Sand Filters Basins (SFBs)**

## **SFB-3.1 Maintenance Personnel**

Maintenance personnel must be qualified to properly maintain SFBs. Inadequately trained personnel can cause additional problems resulting in additional maintenance costs.

## **SFB-3.2 Equipment**

It is imperative that the appropriate equipment and tools are taken to the field with the operations crew. The types of equipment/tools will vary depending on the task at hand. Below is a basic list of tools, equipment, and material(s) that may be necessary to perform maintenance on a SFB:

1. Mowing Tractors
2. Trimmers (extra string)
3. Shovels
4. Rakes
5. All Surface Vehicle (ASVs)
6. Skid Steer
7. Back Hoe
8. Track Hoe/Long Reach Excavator
9. Dump Truck
10. Jet-Vac Machine
11. Engineers Level (laser)
12. Riprap (Minimum - Type M)
13. Geotextile Fabric
14. Erosion Control Blanket(s)
15. Sod
16. Illicit Discharge Cleanup Kits
17. Trash Bags
18. Tools (wrenches, screw drivers, hammers, etc)
19. Confined Space Entry Equipment
20. Approved Stormwater Facility Inspection and Maintenance Plan
21. ASTM C-33 Sand

Some of the items identified above may not be needed for every maintenance operation. However, this equipment and material should be available to the maintenance operations crews should the need arise.

## **SFB-3.3 Safety**

Vertical drops may be encountered in areas located within and around the SFB. Avoid walking on top of retaining walls or other structures having a significant vertical drop. If a vertical drop within the pond is identified as greater than forty-eight (48) inches in height, make the appropriate note/comment on the maintenance inspection form.

## **SFB-3.4 SFB Maintenance Forms**

The SFB Maintenance Form provides a record of each maintenance operation performed by maintenance contractors. The SFB Maintenance Form shall be filled out in the field after the completion of the maintenance operation. Each form shall be reviewed and submitted by the property owner or property manager to the City of Aurora per the requirements of the Inspection and Maintenance Plan. The SFB Maintenance form is located in Appendix E.

## **SFB-3.5 SFB Maintenance Categories and Activities**

A typical SFB Maintenance Program will consist of three broad categories of work: Routine, Minor and Major. Within each category of work, a variety of maintenance activities can be performed on a SFB. A maintenance activity can be specific to each feature within the SFB, or general to the overall facility. This section of the SOP explains each of the categories and briefly describes the typical maintenance activities for a SFB.

A variety of maintenance activities are typical of SFBs. The maintenance activities range in magnitude from routine trash pickup to the reconstruction of the SFB filter media or underdrain system. Below is a description of each maintenance activity, the objectives, and frequency of actions.

## **SFB-3.6 Routine Maintenance Activities**

The majority of this work consists of scheduled mowings, trash and debris pickups for the SFB during the growing season. It also includes activities such as weed control. These activities normally will be performed numerous times during the year. These items typically do not require any prior correspondence with the City of Aurora, however, completed inspection and maintenance forms shall be submitted to the City of Aurora for each inspection and maintenance in accordance with the Inspection and Maintenance Plan.

The Routine Maintenance Activities are summarized below, and further described in the following sections.

**Table SFB-2**

**Summary of Routine Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| Mowing | Twice annually | Excessive grass height/aesthetics | 2”-4” grass height |
| **Trash/Debris Removal** | Twice annually | Trash/debris in SFB | Remove and dispose of trash and debris |
| **Splitter Box/Overflow Outlet Works Cleaning** | As needed - after significant rain events – twice annually minimum | Clogged outlet structure; ponding water | Remove and dispose of  debris/trash/sediment to allow outlet to function properly |
| Woody growth control /Weed removal | Minimum twice annually | Noxious weeds; Unwanted vegetation | Treat w/herbicide or hand pull; consult a local Weed Inspector |

### SFB-3.6.1 Mowing

Routine mowing of the turf grass embankments and turf grass located in the sedimentation chamber (forebay) and embankment is necessary to improve the overall appearance of the SFB, and to ensure proper performance of the sediment chamber. Turf grass should be mowed to a height of two (2) to four (4) inches, and shall be bagged to prevent potential contamination of the filter media.

*Frequency* – Routine - Minimum of twice annually or depending on aesthetics.

### SFB-3.6.2 Trash/Debris Removal

Trash and debris must be removed from the entire SFB area to minimize outlet clogging and to improve aesthetics. This activity must be performed prior to mowing operations.

*Frequency –* Routine – Prior to mowing operations and minimum of twice annually.

SFB-3.6.3 Splitter Box/ Outlet Works Cleaning

Debris and other materials can clog the splitter box/outlet work’s grate or orifice plate(s) and trash rack. This activity must be performed anytime other maintenance activities are conducted to ensure proper operation.

*Frequency* - Routine – After significant rainfall event or concurrently with other maintenance activities.

### SFB- 3.6.4 Woody Growth Control/Weed Removal

Noxious weeds and other unwanted vegetation must be treated as needed throughout the SFB. This activity can be performed either through mechanical means (mowing/pulling) or with herbicide. Consultation with a local Weed Inspector is highly recommended prior to the use of herbicide. Herbicides should be utilized sparingly and as a last resort. All herbicide applications should be in accordance with the manufacturer’s recommendations.

*Frequency –* Routine – As needed based on inspections.

## **SFB-3.7 Minor Maintenance Activities**

#### This work consists of a variety of isolated or small-scale maintenance/operational problems. Most of this work can be completed by a small crew, hand tools, and small equipment. These items require prior approval from the City of Aurora Water Staff. Completed inspection and maintenance forms shall be submitted to the City of Aurora Water Staff for each inspection and maintenance period. In the event the SFB needs to be dewatered, care should be given to ensure sediment, filter material and other pollutants are not discharged. All dewatering activities shall be coordinated with the City of Aurora Water Staff.

**TABLE SFB-3**

**Summary of Minor Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Sediment/Pollutant Removal** | As needed; typically every 1 –2 years | Sediment build-up in sedimentation chamber and filter media; decrease in infiltration rate | Remove and dispose of sediment |
| **Erosion Repair** | As needed, based upon inspection | Rills/gullies on embankments or sedimentation in the forebay | Repair eroded areas &  revegetate; address cause |
| **Jet-Vac/Cleaning Underdrains** | As needed, based upon inspection | Sediment build-up /non-draining system | Clean drains; Jet-Vac if needed |

### 

### SFB-3.7.1 Sediment Removal/Pollutant Removal

Sediment removal is necessary to ensure proper function of the filter media. The infiltration rate of the SFB needs to be checked in order to ensure proper functioning of the SFB. Generally, a SFB should drain completely within twenty-four (24) hours of a storm event. If drain times exceed the twenty-four (24) hour drain time then maintenance of the filter media shall be required.

At a minimum, the top three (3) inches of filter media should be removed at each removal period. Additional amounts of filter media may need to be removed if deeper sections of the filter media are contaminated. New filter media will need to be placed back into the SFB when the total amount of sand removed reaches nine (9) inches. This may take multiple maintenance events to accomplish. It is critical only sand meeting the American Society for Testing and Materials (ASTM) C-33 standard be utilized in the replacement of the filter media. (Note: The update to the UDFCD’s Volume III manual, to be released in late 2010, may have new filter media guidelines).

**ASTM C-33 Sand Standard**

|  |  |
| --- | --- |
| **US Standard Sieve Size (Number)** | **Total Percent Passing (%)** |
| 9.5 mm (3/8 inch) | 100 |
| 4.75 mm (No. 4) | 95-100 |
| 2.36 mm (No. 8) | 80-100 |
| 1.18 mm (No. 16) | 50-85 |
| 6000085mm (No | 25-60 |
| 3000060mm (No | 10-30 |
| 1505030mm (No. | 2-10 |

Other types of sand and soil material may lead to clogging of the SFB. (Note: The update to the UDFCD’s Volume III manual, to be released in late 2010, may have new filter media guidelines). The minor sediment removal activities can typically be addressed with shovels, rakes and smaller equipment.

Stormwater sediments removed from SFBs do not meet the regulatory definition of “hazardous waste”. However, these sediments can be contaminated with a wide array of organic and inorganic pollutants and handling must be done with care to ensure proper removal and disposal. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a licensed landfill for proper disposal. Should a spill occur during transportation, prompt and thorough cleanup and disposal is imperative.

*Frequency* – Non-routine – As necessary, based upon inspections. Sediment removal in the sedimentation chamber (forebay) may be necessary as frequently as every one (1) to two (2) years.

SFB-3.7.2 Erosion Repair

The repair of eroded areas is necessary to ensure the proper functioning of the SFB, to minimize sediment transport, and to reduce potential impacts to other features. Erosion can vary in magnitude from minor repairs to filter media and embankments, to rills, and gullies in the embankments and inflow points. The repair of eroded areas may require the use of excavators, earthmoving equipment, riprap, concrete, and sod. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur. Major erosion repair to the pond embankments, spillways, and adjacent to structures will require consultation with the City of Aurora Water and Engineering Staff.

*Frequency* – Non-routine – As necessary, based upon inspections.

### SFB-3.7.3 Jet-Vac/Clearing Drains

A SFB contains an underdrain system that allows treated stormwater runoff to exit the facility. These underdrain systems can develop blockages that can result in a decrease of hydraulic capacity and also create standing water. Many times the blockage to this infrastructure can be difficult to access and/or clean. Specialized equipment (jet-vac machines) may be necessary to clear debris from these difficult areas.

*Frequency –* Non-routine – As necessary, based upon inspections.

## 

## **SFB-3.8 Major Maintenance Activities**

This work consists of larger maintenance/operational problems and failures within the stormwater management facilities. All of this work requires approval from the City of Aurora to ensure the proper maintenance is performed. This work requires the City of Aurora Water Staff review the original design and construction drawings to assess the situation before approval of the proposed maintenance activities. This work may also require more specialized maintenance equipment, design/details, submittal of plans to the City of Aurora for review and approval, surveying, or assistance through private contractors and consultants. In the event the facility needs to be dewatered, care should be given to ensure sediment, filter material and other pollutants are not discharged. Consultation with the City of Aurora Water Staff is required prior to any dewatering activity.

**Table SFB-4**

**Summary of Major Maintenance Activities**

|  |  |  |  |
| --- | --- | --- | --- |
| **Maintenance Activity** | **Minimum Frequency** | **Look for:** | **Maintenance Action** |
|  |  |  |  |
| **Major Sediment/Pollutant Removal** | As needed – based upon scheduled inspections | Large quantities of sediment in the sedimentation chamber (forebay) and/or filter media; reduced infiltration rate /capacity | Remove and dispose of sediment. Repair vegetation as needed |
| **Major Erosion Repair** | As needed – based upon scheduled inspections | Severe erosion including gullies, excessive soil displacement, areas of settlement, holes | Repair erosion – find cause of problem and address to avoid future erosion |
| **Structural Repair** | As needed – based upon scheduled inspections | Deterioration and/or damage to structural components – broken concrete, damaged pipes & outlet works | Structural repair to restore the structure to its original design |
| **SFB Rebuild** | As needed – due to complete failure of SFB | Removal of filter media and underdrain system | Contact the City of Aurora Water and Engineering Staff |

### 

### SFB-3.8.1 Major Sediment/Pollutant Removal

In very rare cases the filter media of the SFB may be so badly contaminated the entire eighteen (18) inches of the filter media may need to be removed.

Major sediment/pollutant removal consists of removal of large quantities of sediment/filter media. Major sediment removal activities will require larger and more specialized equipment. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur. The sediment/filter media needs to be carefully removed, transported and properly disposed. Vegetated areas need special care to ensure design volumes and grades are preserved or may need to be replaced due to the removal activities. The major sediment removal activities will require surveying with an engineer’s level, and consultation with the City of Aurora Water and Engineering Staff to ensure design volumes/grades are achieved. Stormwater sediments removed from SFBs do not meet the regulatory definition of “hazardous waste”. However, these sediments can be contaminated with a wide array of organic and inorganic pollutants and handling must be done with care to insure proper removal and disposal. Sediments should be transported by motor vehicle only after they are dewatered. All sediments must be taken to a licensed landfill for proper disposal. Should a spill occur during transportation, prompt and thorough cleanup and disposal is imperative.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### SFB-3.8.2 Major Erosion Repair

Major erosion repair consists of filling and revegetating areas of severe erosion. Determining the cause of the erosion as well as correcting the condition that caused the erosion should also be part of the erosion repair. Care should be given to ensure design grades and volumes are preserved. Consult with the City of Aurora Water and Engineering Staff. Extreme care should be taken when utilizing motorized or heavy equipment to ensure damage to the underdrain system does not occur.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### SFB-3.8.3 Structural Repair

A SFB generally includes a splitter box (if no detention component) or concrete outlet structure that can deteriorate or be damaged during the service life of the facility. These structures are constructed of steel and concrete that can degrade or be damaged and may need to be repaired or re-constructed from time to time. Major repairs to structures may require input from a structural engineer and specialized contractors. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to all structural repairs.

*Frequency* – Non-routine – Repair as needed, based upon inspections.

### SFB-3.8.4 SFB Rebuild

In very rare cases a SFB may need to be rebuilt. Generally, the need for a complete rebuild is a result of improper construction, improper maintenance resulting in structural damage to the underdrain system, or extensive contamination of the SFB. Consultation with the City of Aurora Water and Engineering Staff shall take place prior to any rebuild project.


*Frequency* – Non-routine – As needed, based upon inspections.


Reference:


**This plan is adapted from Southeast Metro Stormwater Authority,** *Operation and Maintenance (O & M) Manual,* **and the Douglas County, Colorado,** *Standard Operating Procedure for Extended Detention Basin (EDB) Inspection and Maintenance,* July 2005


**Appendix D**

**Inspection Forms**

****


****



****


****

**Appendix E**

**Maintenance Forms**

****

****

****

**Appendix F**

**Annual Inspection and Maintenance Reporting Form**



Annual Inspection and Maintenance Reporting Form

for

Stormwater Facilities

*(This form shall be submitted to the City of Aurora prior to May 31 of each year along with the Inspection Forms and Maintenance Forms as required for the property/subdivision)*

Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

To: City of Aurora

Aurora Water – Environmental Services

15151 E. Alameda Parkway, Ste. 2500

Aurora, CO 80012

[envservices@auroragov.org](mailto:envservices@auroragov.org)

Re: Certification of Inspection and Maintenance; Submittal of forms

Property/Subdivision Name: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Property Address: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Contact Name: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

I verify that the required stormwater facility inspections and required maintenance have been completed in accordance with the Stormwater Facilities Maintenance Agreement, and the Inspection and Maintenance Plan associated with the above referenced property.

The required Stormwater Facility Inspection and Maintenance forms are hereby provided.

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Name of Party Responsible for Inspection Property Owner

& Maintenance

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Authorized Signature Signature

**Appendix G**

**Inspection and Maintenance Site Plan(s)**

**Check Lists**

**Facilities Map Checklist**

**EDB Checklist**

**GB-GS Checklist**

**BRC/PLD Checklist**

**SFB Checklist**

**Inspection and Maintenance Site Plans**

**Stormwater Facilities Map**

**Checklist for Required Items**

Stormwater facilities map shall include:

* Labels for all streets (includes line work for edge of street and street name)
* Line work for right-of-way lines, lot lines, and tracts
* Line work and labels for all major drainage ways
* Label roadways, developments, etc. adjacent to project site
* Labels for all BMPs being constructed on project site including a summary table when multiple BMPs are present
* Legend for identifying features/line types on drawing (optional)

**Inspection and Maintenance Site Plans**

**Extended Detention Basin (EDB)**

**Checklist for Required Items**

**Plan and Profile Sheet**

Plan view shall include:

* Location and labels for all major features of EDB (inflow structure(s), forebay, micro-pool, trickle channel, access road, outlet work(s), spillway, maintenance access ramps, embankment, etc.)
* Contours
* Other utilities in vicinity of EDB
* Cross-reference to EDB Operation and Maintenance Details sheet
* Line work for right-of-way lines, lot lines, easements, and tracts
* Hatch indicating permanent water elevation in micro-pool.

Profile view shall include:

* Location and labels for all major features of EDB (inflow structure(s), forebay, micro-pool, trickle channel, access road, outlet work(s), spillway, maintenance access ramps, embankment, etc.)
* Invert elevations at major features of EDB (inflow structure(s), forebay, micro-pool, outlet work(s))
* Permanent pool elevation of micro-pool
* Water quality water surface elevation
* Water surface elevation of all applicable storm events
* Label for upper and bottom stages for EDB

**Detail Sheet**

Detail sheet shall include:

* Volume provided by the EDB forebay and micro-pool, including the WQCV
* WQCV drain time
* Seed mix
* Total mow area including approximate mow boundaries on each side of EDB
* Duplicate the following tables from the “Standard Operation Procedure for Extended Detention Basin Inspection and Maintenance” document:
  + Inspection and Maintenance Requirements at Specific EDB Features
  + Summary of Routine Maintenance Activities for an EDB
  + Summary of Minor Maintenance Activities for an EDB
  + Summary of Major Maintenance Activities for an EDB
* Water quality outlet works detail
* Water quality plate detail
* Maintenance access road detail
* Trickle channel typical section
* Forebay edge detail (or cross section) which includes maximum allowed sediment depth in forebay
* Forebay release structure detail
* Spillway detail(s), including cutoff wall

**Inspection and Maintenance Site Plans**

**Grass Swales/Grass Buffers (GS/GB)**

**Checklist for Required Items**

**Plan Sheet**

Plan view shall include:

* Location of grass swale(s) and/or buffer(s)
* Contours
* Line work for right-of-way lines, lot lines, easements, and tracts
* Labels for streets adjacent to grass swale(s)/buffer(s)
* Line work for all storm sewer structures
* Cross-reference to Grass Swale/Buffer Operation and Maintenance Details sheet

**Detail Sheet**

Detail sheet shall include:

* Duplicate the following tables from the “Standard Operation Procedure for Grass Swales/Grass Buffers Inspection and Maintenance” document:
  + Typical Inspection and Maintenance Requirements Matrix
  + Summary of Routine Maintenance Activities
  + Summary of Minor Maintenance Activities
  + Summary of Major Maintenance Activities
* Typical grass swale and/or buffer section including typical horizontal and vertical dimensions, side slopes, subgrade material, and underdrain (if applicable).
* Underdrain details (if applicable) including trench dimensions, perforated PVC dimensions, and trench fill material.

**Inspection and Maintenance Site Plans**

**Bioretention Cell (BRC)**

**aka**

**Porous Landscape Detention (PLD)**

**Checklist for Required Items**

**Plan Sheet**

Plan view shall include:

* Location and labels for all major features of BRC/PLD (inlet pipe, overflow outlet structure, outlet pipe, etc.)
* Line work for underdrains
* Line work for right-of-way lines, lot lines, easements, and tracts
* Contours
* Other utilities in vicinity of BRC/ PLD
* Cross reference to Bioretention Cell/Porous Landscape Detention Operation and Maintenance Details sheet

**Detail Sheet**

* WQCV provided by the BRC/PLD
* WQCV drain time
* Duplicate the following tables from the “Standard Operation Procedure for Bioretention/Porous Landscape Detention Inspection and Maintenance” document:
  + Inspection and Maintenance Requirements at Specific BRC/PLD Features
  + Summary of Routine Maintenance Activities for a BRC/PLD
  + Summary of Minor Maintenance Activities for a BRC/PLD
  + Summary of Major Maintenance Activities for a BRC/PLD
* Overflow outlet box detail/typical cross section
* Typical BRC/PLD cross section (include label for depth of WQCV)
* Underdrain detail including labels for the depth and type of fill materials and diameter of perforated pipe
* Rundown cross section and details (if applicable).

**Inspection and Maintenance Site Plans**

**Sand Filter Basin (SFB)**

**Checklist for Required Items**

**Plan Sheet**

Plan sheet shall include:

* Location and labels for all major features of SFB (inlet pipe, energy dissipation structures, maintenance access road, overflow outlet structure, outlet pipe, spillway, etc.)
* Line work for underdrains
* Line work for right-of-way lines, lot lines, easements, and tracts
* Contours
* Other utilities in vicinity of SFB
* Cross reference to Sand Filter Basin Operation and Maintenance Details sheet

**Detail Sheet**

Detail sheet shall include:

* WQCV provided by the SFB
* WQCV drain time
* Duplicate the following tables from the “Standard Operation Procedure for Sand Filter Basin Inspection and Maintenance” document:
  + Inspection and Maintenance Requirements at Specific SFB Features
  + Summary of Routine Maintenance Activities for a SFB
  + Summary of Minor Maintenance Activities for a SFB
  + Summary of Major Maintenance Activities for a SFB
* Overflow outlet box detail/typical section
* Typical SFB cross section (include label for depth of WQCV)
* Underdrain detail including labels for the depth and type of fill materials and diameter of perforated pipe

**Inspection and Maintenance Site Plans**

**Grass Swales/Grass Buffers (GS/GB)**

**Checklist for Required Items**

**Plan Sheet**

Plan view shall include:

* Location of grass swale(s) and/or buffer(s)
* Contours
* Line work for right-of-way lines, lot lines, easements, and tracts
* Labels for streets adjacent to grass swale(s)/buffer(s)
* Line work for all storm sewer structures
* Cross-reference to Grass Swale/Buffer Operation and Maintenance Details sheet

**Detail Sheet**

Detail sheet shall include:

* Duplicate the following tables from the “Standard Operation Procedure for Grass Swales/Grass Buffers Inspection and Maintenance” document:
  + Typical Inspection and Maintenance Requirements Matrix
  + Summary of Routine Maintenance Activities
  + Summary of Minor Maintenance Activities
  + Summary of Major Maintenance Activities
* Typical grass swale and/or buffer section including typical horizontal and vertical dimensions, side slopes, subgrade material, and underdrain (if applicable).
* Underdrain details (if applicable) including trench dimensions, perforated PVC dimensions, and trench fill material.

1. Design of Stormwater Filtering Systems, Centers for Watershed Protection, December 1996 [↑](#footnote-ref-1)
2. Design of Stormwater Filtering Systems, Centers for Watershed Protection, December 1996 [↑](#footnote-ref-2)
3. Design of Stormwater Filtering Systems, Centers for Watershed Protection, December 1996 [↑](#footnote-ref-3)